## 2019 Consumer Confidence Report

| Water System Name: | Lucky 18 on Rosamond, LLC | Report Date: | June 2020 |
| --- | --- | --- | --- |

We test the drinking water quality for many constituents as required by State and Federal Regulations. This report shows the results of our monitoring for the period of January 1 - December 31, 2019 and may include earlier monitoring data.

Este informe contiene información muy importante sobre su agua potable.  Tradúzcalo ó hable con alguien que lo entienda bien.

| Type of water source(s) in use: | Groundwater from two (2) wells. |  |  |  |
| --- | --- | --- | --- | --- |
| Well 02 West in Rosamond, CA |  |  |  |  |
| Drinking Water Source Assessment information: |  |  |  |  |
| For more information, contact: | Albert Talassazan |  | Phone: | 310-415-9884 |
| TERMS USED IN THIS REPORT: |  |  |  |  |
| Maximum Contaminant Level (MCL): The highest level of a contaminant that is allowed in drinking water. Primary MCLs are set as close to the PHGs (or MCLGs) as is economically and technologically feasible. Secondary MCLs are set to protect the odor, taste, and appearance of drinking water. Maximum Contaminant Level Goal (MCLG): The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs are set by the U.S. Environmental Protection Agency (USEPA). Public Health Goal (PHG): The level of a contaminant in drinking water below which there is no known or expected risk to health. PHGs are set by the California Environmental Protection Agency. Maximum Residual Disinfectant Level (MRDL): The highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants. Maximum Residual Disinfectant Level Goal (MRDLG): The level of a drinking water disinfectant below which there is no known or expected risk to health. MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants. Primary Drinking Water Standards (PDWS): MCLs and MRDLs for contaminants that affect health along with their monitoring and reporting requirements, and water treatment requirements. |  | Secondary Drinking Water Standards (SDWS): MCLs for contaminants that affect taste, odor, or appearance of the drinking water. Contaminants with SDWSs do not affect the health at the MCL levels. Treatment Technique (TT): A required process intended to reduce the level of a contaminant in drinking water. Regulatory Action Level (AL): The concentration of a contaminant which, if exceeded, triggers treatment or other requirements that a water system must follow. Variances and Exemptions: State Board permission to exceed an MCL or not comply with a treatment technique under certain conditions. Level 1 Assessment: A Level 1 assessment is a study of the water system to identify potential problems and determine (if possible) why total coliform bacteria have been found in our water system. Level 2 Assessment: A Level 2 assessment is a very detailed study of the water system to identify potential problems and determine (if possible) why an E. coli MCL violation has occurred and/or why total coliform bacteria have been found in our water system on multiple occasions. ND: not detectable at testing limit ppm: parts per million or milligrams per liter (mg/L) ppb: parts per billion or micrograms per liter (ug/L) ppt: parts per trillion or nanograms per liter (ng/L) ppq: parts per quadrillion or picogram per liter (pg/L) pCi/L: picocuries per liter (a measure of radiation) |  |  |

The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells.  As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.

Contaminants that may be present in source water include:

- Microbial contaminants, such as viruses and bacteria, that may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.

- Inorganic contaminants, such as salts and metals, that can be naturally-occurring or result from urban stormwater runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.

- Pesticides and herbicides, that may come from a variety of sources such as agriculture, urban stormwater runoff, and residential uses.

- Organic chemical contaminants, including synthetic and volatile organic chemicals, that are byproducts of industrial processes and petroleum production, and can also come from gas stations, urban stormwater runoff, agricultural application, and septic systems.

- Radioactive contaminants, that can be naturally-occurring or be the result of oil and gas production and mining activities.

In order to ensure that tap water is safe to drink, the USEPA and the State Water Resources Control Board (State Board) prescribe regulations that limit the amount of certain contaminants in water provided by public water systems.  State Board regulations also establish limits for contaminants in bottled water that provide the same protection for public health.

Tables 1, 2, 3, 4, 5, and 6 list all of the drinking water contaminants that were detected during the most recent sampling for the constituent.  The presence of these contaminants in the water does not necessarily indicate that the water poses a health risk. The State Board allows us to monitor for certain contaminants less than once per year because the concentrations of these contaminants do not change frequently.  Some of the data, though representative of the water quality, are more than one year old.  Any violation of an AL, MCL, MRDL, or TT is asterisked.  Additional information regarding the violation is provided later in this report.

| Table 1 - sampling results showing the detection of coliform bacteria MCLGMicrobiological Typical Source of Bacteria MCL Contaminants (complete if bacteria detected). Total Coliform BacteriaHighest No. of DetectionsNo. of months in violation (state Total Coliform Rule); (In a mo.) 5; 3; 1 positive monthly sample(a); 0; Naturally present in the environment. Fecal Coliform or E. coli (state Total Coliform Rule); (In the year) 0; 0; A routine sample and a repeat sample are total coliform positive, and one of these is also fecal coliform or E. coli positive; 0; Human and animal fecal waste. E. coli (federal Revised Total Coliform Rule); (In the year) 0; 0; (b); 0; Human and animal fecal waste. (a) Two or more positive monthly samples is a violation of the MCL (b) Routine and repeat samples are total coliform-positive and either is E. coli-positive or system fails to take repeat samples following E. coli-positive routine sample or system fails to analyze total coliform-positive repeat sample for E. coli.. |
| --- |
| Table 2 - sampling results showing the detection of Lead and copper |  |  |  |  |  |  |
| Lead and Copper (complete if lead or copper detected in the last sample set) | No. of samples collected | 90th percentile level detected | No. sites exceeding AL | AL | PHG | Typical Source of Contaminant |
| Lead (ppb) (September 2019) | 5 | ND | 0 | 15 | 0.2 | Internal corrosion of household water plumbing systems; discharges from industrial manufacturers; erosion of natural deposits |
| Copper (ppm) (September 2019) | 5 | ND | 0 | 1.3 | 0.3 | Internal corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives |

| TAble 3 - sampling results for sodium and hardness |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Chemical or Constituent (and reporting units) | Sample Date | Level Detected | Range of Detections | MCL | PHG (MCLG) | Typical Source of Contaminant |
| Sodium (ppm) | 2016 | 100 |  | none | none | Salt present in the water and is generally naturally occurring |
| Hardness (ppm) | 2016 | 250 |  | none | none | Sum of polyvalent cations present in the water, generally magnesium and calcium, and are usually naturally occurring |

| TAble 4 - detection of contaminants with a Primary Drinking Water Standard |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Chemical or Constituent (and reporting units) | Sample Date | Level Detected | Range of Detections | MCL [MRDL] | PHG (MCLG) [MRDLG] | Typical Source of Contaminant |
| Gross Alpha (pCi/L) | 2016 | 7.55 |  | 15 | (0) | Erosion of natural deposits |
| Uranium (pCi/L) | 2016 | 8.4 |  | 20 | 0.43 | Erosion of natural deposits |
| Hexavalent Chromium(ppb) | 2014 | 3.3 |  | N/A | N/A | Erosion of natural deposits |
| Radium R-228 (pCi/L) | 2008 | 0.44 | 0.41-0.48 | 5 | (0) | Erosion of natural deposits |
| *Arsenic (ppb) | Quarterly | 32 | 31-33 | 10 | 0.004 | Erosion of natural deposits |
| Barium (ppb) | 2016 | 0.020 |  | 1 | 2 | Erosion of natural deposits |
| Chromium (ppb) | 2016 | ND |  | 50 | (100) | Erosion of natural deposits |
| Fluoride (ppm) | 2016 | 2.8 |  | 2.0 | 1 | Erosion of natural deposits |
| Nitrate as N (ppm) | 2019 | 2.2 |  | 10 | 10 | Erosion of natural deposits; leaching from fertilizer use and septic systems |
| Selenium (ppb) | 2016 | ND |  | 50 | (50) | Erosion of natural deposits |
| TAble 5 - detection of contaminants with a Secondary Drinking Water Standard |  |  |  |  |  |  |
| Chemical or Constituent (and reporting units) | Sample Date | Level Detected | Range of Detections | MCL | PHG (MCLG) | Typical Source of Contaminant |
| Chloride (ppm) | 2016 | 99 |  | 500 | N/A | Runoff from natural deposits |
| Color (Units) | 2016 | 1.0 |  | 15 | N/A | Naturally occurring organic material |
| Iron (ppb) | 2016 | ND |  | 300 | N/A | Runoff/leaching from natural deposits |
| Sulfate (ppm) | 2016 | 190 |  | 500 | N/A | Runoff/leaching from natural deposits |
| TDS (ppm) | 2016 | 630 |  | 1000 | N/A | Runoff/leaching from natural deposits |
| Turbidity (Units) | 2016 | 0.32 |  | 5 | N/A | Soil runoff |
| Zinc (ppm) | 2016 | ND |  | 5.0 | N/A | Runoff/leaching from natural deposits |

Summary Information for Violation of a MCL, MRDL, AL, TT, 
or Monitoring and Reporting Requirement

| VIOLATION OF A MCL, MRDL, AL, TT, OR MONITORING AND REPORTING REQUIREMENT |  |  |  |  |
| --- | --- | --- | --- | --- |
| Violation | Explanation | Duration | Actions Taken to Correct the Violation | Health Effects Language |
| MCL, Average Arsenic | Our water system failed the drinking water standard for arsenic in 2019. | Ongoing | Quarterly monitoring is being conducted. | Some people who drink water containing arsenic in excess of the MCL over many years may experience skin damage or circulatory system problems, and may have an increased risk of getting cancer. |

| VIOLATION OF A MCL, MRDL, AL, TT, OR MONITORING AND REPORTING REQUIREMENT |  |  |  |  |
| --- | --- | --- | --- | --- |
| Violation | Explanation | Duration | Actions Taken to Correct the Violation | Health Effects Language |
| State Primary MCL Coliform (TCR) | The June routine bacteriological sample tested positive for total coliform. We collected three (3) repeat distribution, a storage tank, and a Well sample. All samples tested positive for total coliform. | Month of June 2019 | The certified operator conducted emergency chlorination and flushing of the water system. Seven (7) special samples were collected, all samples tested negative for total coliform. In July, we collected five (5) routine bacteriological samples and all samples tested negative for Total Coliform. | Coliforms are bacteria that are naturally present in the environment and are used as an indicator that other; potentially-harmful, bacteria may be present. Coliforms were found in more samples than allowed and this was a warning of potential problems. |

| VIOLATION OF A MCL, MRDL, AL, TT, OR MONITORING AND REPORTING REQUIREMENT |  |  |  |  |
| --- | --- | --- | --- | --- |
| Violation | Explanation | Duration | Actions Taken to Correct the Violation | Health Effects Language |
| State Primary MCL Coliform (TCR) | Due to a total coliform positive result in October , we were required to collect five (5) routine bacteriological samples in November. All five (5) samples tested positive for total coliform. | Month of November 2019 | The certified operator conducted emergency chlorination and flushing of the water system. Seven (7) special samples were collected, all samples tested negative for total coliform. | Coliforms are bacteria that are naturally present in the environment and are used as an indicator that other; potentially-harmful, bacteria may be present. Coliforms were found in more samples than allowed and this was a warning of potential problems. |

| VIOLATION OF A MCL, MRDL, AL, TT, OR MONITORING AND REPORTING REQUIREMENT |  |  |  |  |
| --- | --- | --- | --- | --- |
| Violation | Explanation | Duration | Actions Taken to Correct the Violation | Health Effects Language |
| State Primary MCL Coliform (TCR) | Due to the total coliform positive results in November, we were required to collect five (5) routine bacteriological samples in December. Three (3) of the five (5) samples tested positive for total coliform. We collected two (2) repeat from Well 02 and the storage tank. Well 02 tested positive for total coliform, the storage tank was negative. | Month of December 2019 | The certified operator conducted emergency chlorination and flushing of the water system. On December 18th, five (5) special samples were collected from the distribution system, all samples tested negative for total coliform. On December 23rd, another round of seven (7) special samples were collected, five (5) from the distribution, Well 02, and the storage tank. All samples tested negative for total coliform. In January, we collected five (5) routine bacteriological samples and all samples tested negative for Total Coliform. | Coliforms are bacteria that are naturally present in the environment and are used as an indicator that other; potentially-harmful, bacteria may be present. Coliforms were found in more samples than allowed and this was a warning of potential problems. |

Summary Information for Federal Revised Total Coliform Rule

Level 1 and Level 2 Assessment Requirements

Level 1 or Level 2 Assessment Requirement not Due to an E. coli MCL Violation

Coliforms are bacteria that are naturally present in the environment and are used as an indicator that other, potentially harmful, waterborne pathogens may be present or that a potential pathway exists through which contamination may enter the drinking water distribution system.  We found coliforms indicating the need to look for potential problems in water treatment or distribution.  When this occurs, we are required to conduct assessment(s) to identify problems and to correct any problems that were found during these assessments.

During the past year we were required to conduct two (2) Level 2 assessment(s).  Two (2) Level 2 assessment(s) were completed.  In addition, we were required to take ten (10) corrective actions and we completed one (1) of these actions.

Level 2 Assessment on June 21, 2019:

During the month of June 2019, one (1) routine sample, collected on June 13th from space #2 in the Family Park, tested positive for total coliform bacteria.  On June 17th, five (5) repeat samples were collected (three (3) samples from the distribution system, one (1) sample from the 90,000 gallon storage tank, and one (1) sample from Well 02).  All five (5) repeat samples tested positive for total coliform bacteria.  After providing emergency disinfection and flushing of the distribution system, seven (7) samples were collected on June 25th (five (5) from the distribution system, one (1) from the storage tank, and one (1) from Well 02) and all seven (7) samples tested negative for total coliform bacteria.

Well 02 may be the cause of bacteriological contamination in June 2019, as the well tested positive for total coliform bacteria on June 17th.

Due to the previous total coliform MCL violation, the State Water Board recommends that the Water System install continuous chlorination treatment at Well 02.

Corrective Actions per letter dated July 09, 2019:

1.  There is no production meter on Well 02’s discharge line.  A production meter must be provided on the well discharge line within 30 days and monthly production data must be reported to the State Water Board in the annual report each year.

2.  Have the 90,000 gallon tank inspected from inside and submit a report (along with pictures) to the State Water Board within 30 days.

3.  Clear the weeds that are growing around Well 02 site, booster pump and other facilities to keep the sites clean and for easy and safe access.  Dying weeds are considered a potential fire hazard.

4.  The Water System should fix the eroded areas under Well 02 concrete pedestal and pressure tank base.

5.  Well 01 is inoperable and no longer an active source of supply.  Within 30 days, the Water System must physically disconnect it from the distribution system and submit photo documentation to the State Water Board.

6.  Since continuous chlorination is not being provided at the wellhead, therefore the Water System needs to have an Emergency Chlorination Plan (ECP) developed.  The ECP would be implemented following bacteriological contamination to help clear the contamination.  Within 30 day, the ECP needs to be prepared and submitted to the State Water Board for review and approval.

7.  A trained Cross-Connection Control Program Specialist should conduct a physical survey of the Water System within 60 days of the letter and submit a report of findings to the State Water Board within 90 days with a plan and time schedule to implement the recommendations of the report.

8.  The current domestic water supply permit was granted to the previous owner, and since he is no longer the owner of the Water System, the Water System is being operated without a valid domestic water supply permit, which is a violation of the California Health & Safety Code.  Based on a review of the State Water Board’s records, a Permit Application package, for change of ownership of the Water System, was sent to you, with a letter dated May 7, 2019.  By July 31, 2019, a Permit Application along with a completed Technical, Managerial, Financial (TMF) Capacity form shall be submitted to this office.

Level 2 Assessment on December 05, 2019:

On November 13, 2019, five (5) routine samples were collected and all samples tested positive for total coliform bacteria.  Considering the system-wide bacteriological contamination and significant rise in bacteria, the State Water Board issued a Tier 1 Boil Water Notice on November 19, 2019, which has not been cancelled yet due to bacteriological quality problems in December 2019.  After providing emergency disinfection and flushing of the distribution system on November 18, 2019, seven (7) samples were collected on November 20, 2019 (five (5) from the distribution system, one (1) from storage tank, and one (1) from Well 02) and all seven samples tested negative for total coliform bacteria.

On December 11, 2019, five (5) routine samples were collected and three (3) samples tested positive for total coliform bacteria.  Two (2) repeat samples were collected on December 12, 2019, from Well 02 and the storage tank.  The storage tank tested negative for total coliform bacteria, however, Well 02 tested positive for total coliform bacteria.

Standing water near the wellhead was noticed during the inspection on December 5, 2019.  The water leak near the wellhead may be the cause of bacteriological failures in November and December of 2019.

Due to the numerous total coliform MCL violations (June 2018, June 2019, November 2019, and December 2019), the State Water Board is going to mandate installation of continuous chlorination treatment at Well 02.

Corrective Actions per letter dated January 8, 2020:

1.  By January 31, 2020, the Water System must install continuous chlorination treatment at Well 02 and submit a permit application along with the Environmental Information Form (EIF), and operations and maintenance plan for the chlorination treatment and chlorination data sheet to the State Water Board.

2.  By January 31, 2020, the Water System shall investigate and fix any water leak that might have caused the standing water and improve the drainage around the well site.  Following completion of this item, submit documentation to the State Water Board.  After fixing the leak, the distribution system should be disinfected and flushed under the supervision of a certied water distribution operator.

3.  Torn screen on the overflow pipe of the storage tank should be fixed.

4.  A production meter must be provided on Well 02’s discharge line within 30 days and monthly production data must be reported to the State Water Board in the annual report each year.

5.  Have the 90,000 gallon tank inspected from inside and submit a report (along with pictures) to the State Water Board within 30 days.

6.  Clear the weeds that are growing around Well 02 site, booster pump and other facilities to keep the sites clean and for easy and safe access.  Dying weeds are considered a potential fire hazard.

7.  The Water System should fix the eroded areas under Well 02 concrete pedestal and pressure tank base.

8.  Well 01 is inoperable and no longer an active source of supply.  It was noticed during the inspection that Well 01 is still connected to the distribution system.  Within 30 days, the Water System must physically disconnect it from the distribution system and submit photo documentation of this work to the State Water Board.

9.  A trained Cross-Connection Control Program Specialist should conduct a physical survey of the Water System within 60 days of the letter and submit a report of findings to the State Water Board within 90 days with a plan and time schedule to implement the recommendations of the report.

10.  The current domestic water supply permit was granted to the previous owner, and since he is no longer the owner of the Water System, the Water System is being operated without a valid domestic water supply permit, which is a violation of the California Health & Safety Code.  Based on a review of the State Water Board’s records, a Permit Application package, for change of ownership of the Water System, was sent to you, with a letter dated May 7, 2019.  By January 31, 2019, a Permit Application along with a completed Technical, Managerial, Financial (TMF) Capacity form shall be submitted to this office.  The water system shall include information about the continuous chlorination treatment at Well 02 in the permit application.

Additional General Information on Drinking Water

Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that the water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the USEPA’s Safe Drinking Water Hotline (1-800-426-4791).

Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care providers. USEPA/Centers for Disease Control (CDC) guidelines on appropriate means to lessen the risk of infection by Cryptosporidium and other microbial contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791).

FOOTNOTES:

Lead: If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children.  Lead in drinking water is primarily from materials and components associated with service lines and home plumbing.  Lucky 18 on Rosamond, LLC is responsible for providing high quality drinking water, but cannot control the variety of materials used in plumbing components.  When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to 2 minutes before using water for drinking or cooking.  If you are concerned about lead in your water, you may wish to have your water tested.  Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline (1-800-426-4701) or at http://www.epa.gov/lead.

Nitrate: Infants below the age of six months who drink water containing nitrate in excess of the MCL may quickly become seriously ill and, if untreated, may die because high nitrate levels can interfere with the capacity of the infant’s blood to carry oxygen.  Symptoms include shortness of breath and blueness of the skin.  High nitrate levels may also affect the oxygen-carrying ability of the blood of pregnant women.

Report prepared by: skOO’kum h2o monitoring, inc. Tehachapi, CA

Consumer Confidence Report

Certification Form

(To be submitted with a copy of the CCR)

| Water System Name: | Lucky 18 on Rosamond, LLC |
| --- | --- |
| Water System Number: | 1500571 |

The water system named above hereby certifies that its Consumer Confidence Report was distributed on ___________________ (date) to customers (and appropriate notices of availability have been given).  Further, the system certifies that the information contained in the report is correct and consistent with the compliance monitoring data previously submitted to the State Water Resources Control Board, Division of Drinking Water (DDW).

| Certified by: | Name: |  |  |  |
| --- | --- | --- | --- | --- |
|  | Signature: |  |  |  |
|  | Title: |  |  |  |
|  | Phone Number: | ( ) | Date: |  |

To summarize report delivery used and good-faith efforts taken, please complete this page by checking all items that apply and fill-in where appropriate:

CCR was distributed by mail or other direct delivery methods (attach description of other direct delivery methods used).

CCR was distributed using electronic delivery methods described in the Guidance for Electronic Delivery of the Consumer Confidence Report (water systems utilizing electronic delivery methods must complete the second page).

“Good faith” efforts were used to reach non-bill paying consumers.  Those efforts included the following methods:

Posting the CCR at the following URL: www.

Mailing the CCR to postal patrons within the service area (attach zip codes used)

Advertising the availability of the CCR in news media (attach copy of press release)

Publication of the CCR in a local newspaper of general circulation (attach a copy of the published notice, including name of newspaper and date published)

Posted the CCR in public places (attach a list of locations)

Delivery of multiple copies of CCR to single-billed addresses serving several persons, such as apartments, businesses, and schools

Delivery to community organizations (attach a list of organizations)

Publication of the CCR in the electronic city newsletter or electronic community newsletter or listserv (attach a copy of the article or notice)

Electronic announcement of CCR availability via social media outlets (attach list of social media outlets utilized)

Other (attach a list of other methods used)

For systems serving at least 100,000 persons:  Posted CCR on a publicly-accessible internet site at the following URL:  www.

For privately-owned utilities:  Delivered the CCR to the California Public Utilities Commission

Consumer Confidence Report

Electronic Delivery Certification

Water systems utilizing electronic distribution methods for CCR delivery must complete this page by checking all items that apply and fill-in where appropriate.

Water system mailed a notification that the CCR is available and provides a direct URL to the CCR on a publicly available website where it can be viewed (attach a copy of the mailed CCR notification). URL: www.___________________________________________________________

Water system emailed a notification that the CCR is available and provides a direct URL to the CCR on a publicly available site on the Internet where it can be viewed (attach a copy of the emailed CCR notification). URL: www.________________________________________________

Water system emailed the CCR as an electronic file email attachment.

Water system emailed the CCR text and tables inserted or embedded into the body of an email, not as an attachment (attach a copy of the emailed CCR).

Requires prior DDW review and approval. Water system utilized other electronic delivery method that meets the direct delivery requirement.

Provide a brief description of the water system’s electronic delivery procedures and include how the water system ensures delivery to customers unable to receive electronic delivery.

This form is provided as a convenience and may be used to meet the certification requirement of
 section 64483(c), California Code of Regulations.