## 2017 Consumer Confidence Report

|  |  |  |  |
| --- | --- | --- | --- |
| Water System Name: | **Mettler Valley Mutual Water Company** | Report Date: | October 1, 2018 |

*We test the drinking water quality for many constituents as required by state and federal regulations. This report shows the results of our monitoring for the period of January 1 - December 31, 2017 and may include earlier monitoring data.*

**Este informe contiene información muy importante sobre su agua potable. Tradúzcalo ó hable con alguien que lo entienda bien.**

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Type of water source(s) in use: | | Well | | | | | | |
| Name & general location of source(s): | | | Well #1, 28115 West Avenue C-6, Lancaster, CA 93536 | | | | | |
| Well #2, Alternate Source (in process of becoming operational) | | | | | | | | |
| Located at 28115 West Avenue C-6, Lancaster, CA 93536 | | | | | | | | |
| Drinking Water Source Assessment information: | | | | Assessments of the drinking water sources for Mettler Valley | | | | |
| Mutual Water Company were completed in March and April 2002. The sources are considered most vulnerable to the | | | | | | | | |
| following activities not associated with any detected contaminants: Septic systems – Low density (<1/acre); | | | | | | | | |
| Wells – Agricultural/Irrigation. A copy of the assessment may be viewed at : Los Angeles County Environmental Health | | | | | | | | |
| Drinking Water Program at 5050 Commerce Drive, Baldwin Park, CA 91706-1423. You may request a summary of the | | | | | | | | |
| Assessment be sent to you by calling (626) 430-5420. | | | | | | | | |
| Time and place of regularly scheduled board meetings for public participation: | | | | | | | Shareholders are welcome to attend | |
| Board meetings. For dates and times, please contact Debbie Farrow, Secretary. | | | | | | | | |
| For more information, contact: | Debbie Farrow | | | | | Phone: | | (661) 724-3026 |
| **TERMS USED IN THIS REPORT** | | | | | | | | |
| **Maximum Contaminant Level (MCL)**: The highest level of a contaminant that is allowed in drinking water. Primary MCLs are set as close to the PHGs (or MCLGs) as is economically and technologically feasible. Secondary MCLs are set to protect the odor, taste, and appearance of drinking water.  **Maximum Contaminant Level Goal (MCLG)**: The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs are set by the U.S. Environmental Protection Agency (U.S. EPA).  **Public Health Goal (PHG)**: The level of a contaminant in drinking water below which there is no known or expected risk to health. PHGs are set by the California Environmental Protection Agency.  **Maximum Residual Disinfectant Level (MRDL)**: The highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.  **Maximum Residual Disinfectant Level Goal (MRDLG)**:The level of a drinking water disinfectant below which there is no known or expected risk to health. MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants.  **Primary Drinking Water Standards (PDWS)**: MCLs and MRDLs for contaminants that affect health along with their monitoring and reporting requirements, and water treatment requirements. | | | | | **Secondary Drinking Water Standards (SDWS)**:MCLs for contaminants that affect taste, odor, or appearance of the drinking water. Contaminants with SDWSs do not affect the health at the MCL levels.  **Treatment Technique (TT)**: A required process intended to reduce the level of a contaminant in drinking water.  **Regulatory Action Level (AL)**: The concentration of a contaminant which, if exceeded, triggers treatment or other requirements that a water system must follow.  **Variances and Exemptions**: State Board permission to exceed an MCL or not comply with a treatment technique under certain conditions.  **Level 1 Assessment**: A Level 1 assessment is a study of the water system to identify potential problems and determine (if possible) why total coliform bacteria have been found in our water system.  **Level 2 Assessment**: A Level 2 assessment is a very detailed study of the water system to identify potential problems and determine (if possible) why an *E. coli* MCL violation has occurred and/or why total coliform bacteria have been found in our water system on multiple occasions.  **ND**: not detectable at testing limit  **ppm**: parts per million or milligrams per liter (mg/L)  **ppb**: parts per billion or micrograms per liter (µg/L)  **ppt**: parts per trillion or nanograms per liter (ng/L)  **ppq**: parts per quadrillion or picogram per liter (pg/L)  **pCi/L**: picocuries per liter (a measure of radiation) | | | |

**The sources of drinking water** (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells. As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.

**Contaminants that may be present in source water include:**

* *Microbial contaminants*, such as viruses and bacteria, that may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.
* *Inorganic contaminants*, such as salts and metals, that can be naturally-occurring or result from urban stormwater runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.
* *Pesticides and herbicides*, that may come from a variety of sources such as agriculture, urban stormwater runoff, and residential uses.
* *Organic chemical contaminants*, including synthetic and volatile organic chemicals, that are byproducts of industrial processes and petroleum production, and can also come from gas stations, urban stormwater runoff, agricultural application, and septic systems.
* *Radioactive contaminants*, that can be naturally-occurring or be the result of oil and gas production and mining activities.

**In order to ensure that tap water is safe to drink**, the U.S. EPA and the State Water Resources Control Board (State Board) prescribe regulations that limit the amount of certain contaminants in water provided by public water systems. State Board regulations also establish limits for contaminants in bottled water that provide the same protection for public health.

**Tables 1, 2, 3, 4, 5, and 6 list all of the drinking water contaminants that were detected during the most recent sampling for the constituent**. The presence of these contaminants in the water does not necessarily indicate that the water poses a health risk. The State Board allows us to monitor for certain contaminants less than once per year because the concentrations of these contaminants do not change frequently. Some of the data, though representative of the water quality, are more than one year old. Any violation of an AL, MCL, MRDL, or TT is asterisked. Additional information regarding the violation is provided later in this report.

|  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Table 1 – SAMPLING RESULTS SHOWING the detection of coliform bacteria | | | | | | | | | | | |
| **Microbiological Contaminants** (complete if bacteria detected) | | **Highest No. of Detections** | | **No. of Months in Violation** | | MCL | | | **MCLG** | **Typical Source of Bacteria** | |
| Total Coliform Bacteria (state Total Coliform Rule) | | (In a mo.)  0 | | 0 | | 1 positive monthly sample | | | 0 | Naturally present in the environment | |
| Fecal Coliform or *E. coli* (state Total Coliform Rule) | | (In the year)  0 | | 0 | | A routine sample and a repeat sample are total coliform positive, and one of these is also fecal coliform or *E. coli* positive | | | 0 | Human and animal fecal waste | |
| *E. coli*  (federal Revised Total Coliform Rule) | | (In the year)  0 | | 0 | | (a) | | | 0 | Human and animal fecal waste | |
| (a) Routine and repeat samples are total coliform-positive and either is *E. coli*-positive or system fails to take repeat samples following *E. coli*-positive routine sample or system fails to analyze total coliform-positive repeat sample for *E. coli*. | | | | | | | | | | | |
| Table 2 – SAMPLING RESULTS SHOWING THE detection of Lead and copper | | | | | | | | | | | |
| Lead and Copper (complete if lead or copper detected in the last sample set) | **Sample Date** | | **No. of Samples Collected** | | **90th Percentile Level Detected** | **No. Sites Exceeding AL** | **AL** | **PHG** | **No. of Schools Requesting Lead Sampling** | | **Typical Source of Contaminant** |
| Lead (ppb) | 9-22-17  to  9-25-17 | | 5 | | 7.0 | 0 | 15 | 0.2 | 0 | | Internal corrosion of household water plumbing systems; discharges from industrial manufacturers; erosion of natural deposits |
| Copper (ppm) | 9-22-17 to  9-25-17 | | 5 | | 0.138 | 0 | 1.3 | 0.3 | Not applicable | | Internal corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives |

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| TAble 3 – SAMPLING RESULTS FOR sodium and hardness | | | | | | | |
| **Chemical or Constituent** (and reporting units) | **Sample Date** | | **Level Detected** | **Range of Detections** | **MCL** | **PHG (MCLG)** | **Typical Source of Contaminant** |
| Sodium (ppm) | 4-11-16 | | 32 |  | none | none | Salt present in the water and is generally naturally occurring |
| Hardness (ppm) | 4-11-16 | | 160 |  | none | none | Sum of polyvalent cations present in the water, generally magnesium and calcium, and are usually naturally occurring |
| **TAble 4 – detection of contaminants with a Primary Drinking Water Standard** | | | | | | | |
| **Chemical or Constituent** (and reporting units) | | **Sample Date** | **Level Detected** | **Range of Detections** | **MCL [MRDL]** | **PHG (MCLG) [MRDLG]** | **Typical Source of Contaminant** |
| Turbidity (NTU) | | 4-11-16 | 0.42 |  | TT | N/A | Soil runoff |
| Gross Beta (pCi/L) | | 11-3-09 | 3.1 |  | 50 | (0) | Decay of natural and m an-made deposits |
| Gross Alpha Particle Activity (pCi/L) | | 1-3-17  11-8-17 | 6.55 | 6.55-6.55 | 15 | (0) | Erosion of natural deposits |
| Uranium (pCi/L) | | 1-3-17  11-8-17 | 6.75 | 6.7-6.8 | 20 | 0.43 | Erosion of natural deposits |
| Arsenic (ppb) | | 1-3-17  3-6-17  4-6-17  7-11-17  10-3-17 | **14.60 \*** | **13-15 \*** | 10 | 0.004 | Erosion of natural deposits; runoff from orchards; glass and electronics production wastes |
| Fluoride (ppm) | | 4-11-16 | 0.65 |  | 2.0 | 1 | Erosion of natural deposits; water additive which promotes strong teeth; discharge from fertilizer and aluminum factories |
| Hexavalent Chromium (ppb) | | 11-8-17 | 1.3 |  | N/A | N/A | Discharge from electroplating factories, leather tanneries, wood preservation, chemical synthesis, refractory production, and textile manufacturing facilities; erosion of natural deposits.  **NOTE**: There is currently no MCL for hexavalent chromium. The previous MCL of 0.010 mg/L (10 ppb) was withdrawn on 9-11-17. However, any hexavalent chromium results above the detection limit of 1 ppb should be reported. |
| Nitrate (as nitrogen, N) (ppm) | | 12-5-17 | 3.6 |  | 10 | 10 | Runoff and leaching from fertilizer use; leaching from septic tanks and sewage; erosion of natural deposits |
| ***\* Any violation of an MCL, MRDL, or TT is asterisked. Additional information regarding the violation is provided later in this report.*** | | | | | | | |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TAble 5 – detection of contaminants with a Secondary Drinking Water Standard** | | | | | | |
| **Chemical or Constituent** (and reporting units) | **Sample Date** | **Level Detected** | **Range of Detections** | **MCL** | **PHG (MCLG)** | Typical Source of Contaminant |
| Color (Units) | 4-11-16 | 1.0 |  | 15 | N/A |  |
| Turbidity (NTU) | 4-11-16 | 0.42 |  | 5 | N/A | Soil runoff |
| Total Dissolved Solids (TDS) (ppm) | 4-11-16 | 300 |  | 1000 | N/A | Runoff/leaching from natural deposits |
| Specific Conductance (umhos/cm) | 4-11-16 | 416 |  | 1600 | N/A | Substances that form ions when in water; seawater influence |
| Chloride (ppm) | 4-11-16 | 8.3 |  | 500 | N/A | Substances that form ions when in water; seawater influence |
| Sulfate (ppm) | 4-11-16 | 22 |  | 500 | N/A | Substances that form ions when in water; seawater influence |
| ***\* Any violation of an MCL, MRDL, or TT is asterisked. Additional information regarding the violation is provided later in this report.*** | | | | | | |

**Summary Information for Violation of a MCL, MRDL, AL, TT,  
or Monitoring and Reporting Requirement**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **VIOLATION OF A MCL, MRDL, AL, TT, OR MONITORING AND REPORTING REQUIREMENT** | | | | |
| **Violation** | **Explanation** | **Duration** | **Actions Taken to Correct the Violation** | **Health Effects Language** |
| Arsenic | Our water system has failed the drinking water standard for Arsenic. The State of California lowered the Maximum Contaminant Level (MCL) for Arsenic from 50 ppb to 10ppb in 2006. The level of Arsenic in our water has remained at about the same level throughout the years.  We continue to comply with Health Dept. direction by sampling for Arsenic quarterly (as shown in preceding Table 4), and our test results continue to be above the MCL. | 2006 – Present | We are continuing our work with engineering firm NV5, U.S. Dept. of Agriculture (USDA), and California Dept. of Public Health (CDPH) personnel in obtaining a grant to resolve our Arsenic problem and also to address our aging infrastructure issues. We are excited to report that we were recently informed that a grant has been approved, and preparation work is now in progress to begin the planning phase and implementation of Arsenic remediation and aging infrastructure issues! | Some people who drink water containing arsenic in excess of the MCL over many years may experience skin damage or circulatory system problems, and may have an increased risk of getting cancer. |

**Additional General Information on Drinking Water**

Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants. The presence of contaminants does not necessarily indicate that the water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the U.S. EPA’s Safe Drinking Water Hotline (1-800-426-4791).

Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care providers. U.S. EPA/Centers for Disease Control (CDC) guidelines on appropriate means to lessen the risk of infection by *Cryptosporidium* and other microbial contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791).

Lead-Specific Language for Community Water Systems: If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children. Lead in drinking water is primarily from materials and components associated with service lines and home plumbing. Mettler Valley Mutual Water Company is responsible for providing high quality drinking water, but cannot control the variety of materials used in plumbing components. When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to 2 minutes before using water for drinking or cooking. [Optional: If you do so, you may wish to collect the flushed water and reuse it for another beneficial purpose, such as watering plants.] If you are concerned about lead in your water, you may wish to have your water tested. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline (1-800-426-4791) or at <http://www.epa.gov/lead>.

**Water Conservation Tips for Consumers**

Did you know that the average U.S. household uses approximately 400 gallons of water per day or 100 gallons per person per day? Fortunately, there are many low-cost and no-cost ways to conserve water. Small changes can make a big difference – try one today and soon it will become second nature.

\* Take short showers – a 5-minute shower uses 4 to 5 gallons of water compared to up to 50 gallons for a bath.

\* Shut off water while brushing your teeth, washing your hair, and shaving and save up to 500 gallons a month.

\* Use a water-efficient showerhead. They are inexpensive, easy to install, and can save you up to 750 gallons a

month.

\* Run your clothes washer and dishwasher only when they are full. You can save up to 1,000 gallons a month.

\* Water plants only when necessary.

\* Fix leaking toilets and faucets. Faucet washers are inexpensive and take only a few minutes to replace. To

check your toilet for a leak, place a few drops of food coloring in the tank and wait. If it seeps into the toilet

bowl without flushing, you have a leak. Fixing it or replacing it with a new, more efficient model can save up

to 1,000 gallons a month.

\* Adjust sprinklers so only your lawn is watered. Apply water only as fast as the soil can absorb it and during the

cooler parts of the day to reduce evaporation.

\* Teach your kids about water conservation to ensure a future generation that uses water wisely. Make it a family

effort to reduce next month’s water bill!

\* Visit www.epa.gov/watersense for more information.

**Source Water Protection Tips for Consumers**

Protection of drinking water is everyone’s responsibility. You can help protect your community’s drinking water source in several ways:

\* Eliminate excess use of lawn and garden fertilizers and pesticides – they contain hazardous chemicals

that can reach your drinking water source.

\* Pick up after your pets.

\* Properly maintain your septic system to reduce leaching to water system.

\* Dispose of chemicals properly, i.e., take used motor oil to a recycling center.