## 2023 Consumer Confidence Report

| Water System Name: | Sunnyside Farms Mutual Water Company | Report Date: | June 5, 2024 |
| --- | --- | --- | --- |

We test the drinking water quality for many constituents as required by state and federal regulations.  This report shows the results of our monitoring for the period of January 1 to December 31, 2023 and may include earlier monitoring data.

Este informe contiene información muy importante sobre su agua para beber.  Favor de comunicarse  Los Angeles County Public Health Department a (626)430-5420  para asistencia en español.  This Report Statement can be obtained, translated into Five Non-English Languages (Spanish, Mandarin, Tagalog, Vietnamese, and Hmong) via the Los Angeles County Department of Public Health.

| Type of water source(s) in use: |  | Ground-Water and Treated Surface Water as a secondary source of supply |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Name & general location of source(s): |  |  | Community ground-water wells and California Aqueduct water purchased from |  |  |  |  |
| Antelope Valley East Kern Water Agency (AVEK) |  |  |  |  |  |  |  |
| Drinking Water Source Assessment information: |  |  |  | Ground-water is vulnerable to nitrates from septic tanks and fertilizer use. |  |  |  |
| Water storage tanks may be vulnerable to contamination. |  |  |  |  |  |  |  |
| Time and place of regularly scheduled board meetings for public participation: |  |  |  |  | Board Meetings are held on the second |  |  |
| Monday of each month and are open to Shareholders and Residents with advance notification. |  |  |  |  |  |  |  |
| For more information, contact: | Jeanne Miller via email at ssfmwc@gmail.com or |  |  |  |  | Phone: | (661) 947-3437 (no texts) |

| TERMS USED IN THIS REPORT |  |
| --- | --- |
| Maximum Contaminant Level (MCL): The highest level of a contaminant that is allowed in drinking water. Primary MCLs are set as close to the PHGs (or MCLGs) as is economically and technologically feasible. Secondary MCLs are set to protect the odor, taste, and appearance of drinking water. Maximum Contaminant Level Goal (MCLG): The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs are set by the U.S. Environmental Protection Agency (U.S. EPA). Public Health Goal (PHG): The level of a contaminant in drinking water below which there is no known or expected risk to health. PHGs are set by the California Environmental Protection Agency. Maximum Residual Disinfectant Level (MRDL): The highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants. Maximum Residual Disinfectant Level Goal (MRDLG): The level of a drinking water disinfectant below which there is no known or expected risk to health. MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants. Primary Drinking Water Standards (PDWS): MCLs and MRDLs for contaminants that affect health along with their monitoring and reporting requirements, and water treatment requirements. | Secondary Drinking Water Standards (SDWS): MCLs for contaminants that affect taste, odor, or appearance of the drinking water. Contaminants with SDWSs do not affect the health at the MCL levels. Treatment Technique (TT): A required process intended to reduce the level of a contaminant in drinking water. Regulatory Action Level (AL): The concentration of a contaminant which, if exceeded, triggers treatment or other requirements that a water system must follow. Variances and Exemptions: Permissions from the State Water Resources Control Board (State Board) to exceed an MCL or not comply with a treatment technique under certain conditions. Level 1 Assessment: A Level 1 assessment is a study of the water system to identify potential problems and determine (if possible) why total coliform bacteria have been found in our water system. Level 2 Assessment: A Level 2 assessment is a very detailed study of the water system to identify potential problems and determine (if possible) why an E. coli MCL violation has occurred and/or why total coliform bacteria have been found in our water system on multiple occasions. ND: not detectable at testing limit ppm: parts per million or milligrams per liter (mg/L) ppb: parts per billion or micrograms per liter (µg/L) ppt: parts per trillion or nanograms per liter (ng/L) ppq: parts per quadrillion or picogram per liter (pg/L) pCi/L: picocuries per liter (a measure of radiation) |

The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells.  As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.

Contaminants that may be present in source water include:

- Microbial contaminants, such as viruses and bacteria, that may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.

- Inorganic contaminants, such as salts and metals, that can be naturally-occurring or result from urban stormwater runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.

- Pesticides and herbicides, that may come from a variety of sources such as agriculture, stormwater runoff, and residential uses.

- Organic chemical contaminants, including synthetic and volatile organic chemicals, that are byproducts of industrial processes and petroleum production, and can also come from gas stations, storm-water runoff, agricultural application, and septic systems.

- Radioactive contaminants, that can be naturally-occurring or be the result of oil and gas production and mining activities.

In order to ensure that tap water is safe to drink, the U.S. EPA and the State Board prescribe regulations that limit the amount of certain contaminants in water provided by public water systems.  The U.S. Food and Drug Administration regulations and California law also establish limits for contaminants in bottled water that provide the same protection for public health.

The Tables below list all of the drinking water contaminants that were detected during the most recent sampling for the constituent.  The presence of these contaminants in the water does not necessarily indicate that the water poses a health risk.  The State Board allows us to monitor for certain contaminants less than once per year because the concentrations of these contaminants do not change frequently.  Some of the data, though representative of the water quality, are more than one year old.  Any violation of an AL, MCL, MRDL, or TT is asterisked.  Additional information regarding the violation is provided later in this report.

| Table 1 – SAMPLING RESULTS SHOWING the detection of coliform bacteria |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Microbiological Contaminants (complete if bacteria detected) |  | Highest No. of Detections |  | No. of Months in Violation |  | MCL |  |  |  |  | MCLG | Typical Source of Bacteria |
| Total Coliform Bacteria (state Total Coliform Rule) |  | (0) |  | 0 |  | 1 positive monthly sample (a) |  |  |  |  | 0 | Naturally present in the environment |
| Fecal Coliform or E. coli (state Total Coliform Rule) |  | (0) |  | 0 |  | A routine sample and a repeat sample are total coliform positive, and one of these is also fecal coliform or E. coli positive |  |  |  |  | 0 | Human and animal fecal waste |
| E. coli (federal Revised Total Coliform Rule) |  | (0) |  | 0 |  | (b) |  |  |  |  | 0 | Human and animal fecal waste |
| (a) Two or more positive monthly samples is a violation of the MCL (b) Routine and repeat samples are total coliform-positive and either is E. coli-positive or system fails to take repeat samples following E. coli-positive routine sample or system fails to analyze total coliform-positive repeat sample for E. coli. |  |  |  |  |  |  |  |  |  |  |  |  |
| Table 2 – SAMPLING RESULTS SHOWING THE detection of Lead and copper |  |  |  |  |  |  |  |  |  |  |  |  |
| Lead and Copper (complete if lead or copper detected in the last sample set) | Sample Date |  | No. of Samples Collected |  | 90th Percentile Level Detected |  | No. Sites Exceeding AL | AL | PHG | No. of Schools Requesting Lead Sampling |  | Typical Source of Contaminant |
| Lead (ppb) | 2023 |  | 5 |  | 13 |  | 1* | 15 | 0.2 | Not Applicable |  | Internal corrosion of household water plumbing systems; erosion of natural deposits |
| Copper (ppm) | 2023 |  | 5 |  | 0.28 |  | 0 | 1.3 | 0.3 | Not Applicable |  | Internal corrosion of household plumbing systems; erosion of natural deposits. |

| TAble 3 – SAMPLING RESULTS FOR sodium and hardness |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Chemical or Constituent (and reporting units) | Sample Source |  | Level Detected | Range of Detections | MCL | PHG (MCLG) | Typical Source of Contaminant |
| Sodium (ppm) Sampled 2023 | AVEK Wells |  | 47 68 | 27-73 | None | None | Salt present in the water and is generally naturally occurring |
| Hardness (ppm) Sampled 2023 | AVEK Wells |  | 100 397 | 346-383 | None | None | Sum of polyvalent cations present in the water, generally magnesium and calcium, and are usually naturally occurring |
| TAble 4 – detection of contaminants with a Primary Drinking Water Standard |  |  |  |  |  |  |  |
| Chemical or Constituent (and reporting units) |  | Sample Source | Level Detected | Range of Detections | MCL [MRDL] | PHG (MCLG) [MRDLG] | Typical Source of Contaminant |
| Bromate ug/L |  | AVEK | <1 | ND-3.6 | 10 | 0.1 | By-product of drinking water disinfection |
| Chlorine mg/L 2023 |  | AVEK | 1.12 | 0.21-1.90 | 4.0 | 4.0 | By-product of drinking water disinfection |
| Chromium ug/L Sampled 2021-2023 |  | AVEK Wells | ND 1.9 | ND-4.2 | 50 | 0.02 | Discharge from manufacturing: Erosion of natural deposits |
| Copper ug/L |  | AVEK | ND |  | 1000 | 170 | Erosion from natural deposits |
| Fluoride mg/L Sampled 2023 |  | AVEK Wells | 0.12 0.2 | 0.2 | 2 | 1 | Erosion of natural deposits; discharge from fertilizer factories |
| Nickel ug/L Sampled 5-20-20 |  | Well #2 | 6 |  | 100 | 12 | Erosion of natural deposits; discharge from metal factories |
| Nitrate (as N) mg/L Quarterly in 2023 |  | AVEK Wells | <1 6.7 | 0.84 5.2-9.8 | 10 | 10 | Run off or leaching from fertilizer; leaching from septic tanks; erosion of natural deposits |
| Selenium ug/L 2023 |  | Wells | ND | ND-7 | 50 | 30 | Erosion of natural deposits; Rnoff from livestock lots |
| Total Trihalomethanes ug/L sampled 2023 |  | AVEK System | 46 4 | 9.5-56 ND-4 | 80 | N/A | By-product of drinking water disinfection |
| Haloacetic Acids ug/L System sampled 2023 |  | AVEK System | 14 3 | ND-24 2-3 | 60 | N/A | By-product of drinking water disinfection |
| Uranium pCi/L 2022-23 |  | AVEK | ND-3.5 | 3.5 | 20 | N/A | Erosion of natural deposits |
| Gross Alpha pCi/L 2023 |  | AVEK Wells | 5.7 4.06 | 5.7 | 15 | N/A | Erosion of natural deposits |
| TAble 5 – detection of contaminants with a Secondary Drinking Water Standard There are no PHGs, MCLGs for these constituents because secondary MCLs are set on the basis of aesthetics. |  |  |  |  |  |  |  |
| Chemical or Constituent (and reporting units) |  | Sample Source | Level Detected | Range of Detections | SMCL | PHG (MCLG) | Typical Source of Contaminant |
| Chloride mg/L Sampled 2023 |  | AVEK Wells | 71 110 | 91-124 | 500 | N/A | Run-off/leaching from natural deposits |
| Color 2023 |  | AVEK Wells | <5 4 | ND-12 | 15 | N/A | Naturally occurring organic materials |
| Iron 2023 |  | Wells | 197 | 40-480* | 300 | N/A | Leaching from natural deposits. Industrial wastes |
| Sulfate mg/L Sampled 2023 |  | AVEK Wells | 58 241 | 180-282 | 500 | N/A | Run-off/leaching from natural deposits |
| Total Organic Carbon mg/L 2023 |  | AVEK | 2.0 | 0.8-2.9 | N/A | N/A | Water Treatment Technique; natural sources |
| Specific Conductance umhos Sampled 2023 |  | AVEK Wells | 460 1082 | 460-470 997-1210 | 1600 | N/A | Substances that for ions when in water |
| Total Dissolved Solids mg/L Sampled 2023 |  | AVEK Wells | 250 733 | 660-830 | 1000 | N/A | Run-off/leaching from natural deposits |
| Turbidity units Sampled 2023 |  | AVEK Wells | <1 2.98 | 0.03-0.19 0.1-8.7* | 5 | N/A | Soil Run-off |
| Vanadium µg/L Sampled 2023 |  | Wells | 3 | 3-4 | 15 | N/A | Leaching from natural deposits; industrial wastes |
| Zinc ug/L 2023 |  | AVEK Wells | 580 10 | N/D-20 | 5000 | N/A | Run-off/leaching from natural deposits; industrial wastes |
| TAble 6 – detection of UNREGULATED CONTAMINANTS |  |  |  |  |  |  |  |
| Chemical or Constituent (and reporting units) |  | Sample Source | Level Detected | Range of Detections | Notification Level |  | Informational data for Consumers |
| Calcium mg/L Sampled 2023 |  | AVEK Wells | 22 110 | 99-118 | No Standard |  | Leaching/erosion from natural deposits |
| Magnesium mg/L Sampled 2023 |  | AVEK Wells | 12 30 | 28-32 | No Standard |  | Leaching/erosion from natural deposits |
| Potassium mg/L Sampled 5/20/20 |  | Wells | 1.7 | 1-2 | No Standard |  | Leaching/erosion from natural deposits |
| pH units 2023 |  | AVEK Wells | 6.9 7.74 | 6.5-7.2 7.7-7.8 | No Standard |  | The acidity or alkalinity of water on a scale on which 7 is neutral, lower = more acid and higher = more alkaline. |
| Bicarbonate Alkalinity as HCO3 mg/L 5-20-20 |  | AVEK Wells | 62 137 | 130-150 | No Standard |  | Aids in neutralizing the acids in water, therefore helping to balance the pH |
| Total Alkalinity mg/L Sampled 2023 |  | AVEK Wells | 55 120 | 110-130 | No Standard |  | Indicative of the water’s ability to neutralize acid. |
| Aggressiveness Index Sampled 5/30/20 |  | Wells | 0.4 | 0.3-0.5 | No Standard |  | Moderately aggressive on the scale |

Table 7. Violation of a MCL, MRDL, AL, TT or Monitoring Reporting Requirement

| Violation | Explanation | Duration | Actions Taken to Correct Violation | Health Effects Language |
| --- | --- | --- | --- | --- |
| Iron | The casing in well #1 is degrading. | One sample in May 2023 | The well has been sleeved and a sand separator added to remove sand and iron particles from the water before it enters the distribution system. Water samples are now tested quarterly to monitor Iron. | Iron was found at levels that exceed the secondary MCL. The Iron MCL was set to protect you against unpleasant aesthetic affects such as color, taste, odor and the staining of plumbing fixtures (e.g., tubs and sinks), and clothing while washing. Violating this MCL does not pose a risk to public health. |
| Turbidity | Sand in water from well #3 | One sample in May 2023 | A sand separator was added to remove sand particles from the water before it enters the distribution system. Water is being sampled quarterly to monitor turbidity. | Turbidity is Secondary Drinking Water Standards and has found no health effects. However, high levels of turbidity can interfere with disinfection and provide a medium for microbial growth. Turbidity may indicate the presence of disease-causing organisms. These organisms include bacteria, viruses, and parasites that can cause symptoms such as nausea, cramps, diarrhea and associated headaches |
| Lead | One of the samples taken from inside the homes of 5 residences showed a higher than acceptable level of lead. | Unknown | The resident was notified of the lead content in their water and was advised to replace the fixture the water sample had been taken from. | Infants and children who drink water containing lead in excess of the action level may experience delays in their physical or mental development. Children may show slight deficits in attention span and learning abilities. Adults who drink this water over many years may develop kidney problems or high blood pressure. |

Additional General Information on Drinking Water

Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that the water poses a health risk.  More information about contaminants and potential health effects can be obtained by calling the U.S. EPA’s Safe Drinking Water Hotline (1-800-426-4791). Some people may be more vulnerable to contaminants in drinking water than the general population.  Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections.  These people should seek advice about drinking water from their health care providers.  U.S. EPA/Centers for Disease Control (CDC) guidelines on appropriate means to lessen the risk of infection by Cryptosporidium and other microbial contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791).   If you are concerned about lead in your water, you may wish to have your water tested.  Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline (1-800-426-4791) or at http://www.epa.gov/lead.

The water in our distribution system is a blend of AVEK water and ground-water from our five community wells. More information on AVEK’s water can be found at https://www.avek.org/2023-annual-water-quality-report-los-angeles-county-system The laboratory results from our water testing are available for review, upon request.  If you have questions regarding the water quality testing or blending process, contact Tony at Morrison Well Maintenance at 661-466-6031.

Our ground water is blended with AVEK’s treated surface water in the distribution system in order to meet consumer demand. It also acts to ensure that we do not pump over our allotment of ground-water and has the added benefit of reducing the effects of hard water on plumbing fixtures. AVEK’s rate is currently $752 per acre foot ($2.30 per thousand gallons) and will be increasing by up to 7% on July 1st, 2024. Sunnyside Farms MWC was allotted only 74 acre feet per year in the groundwater litigation, the equivalent of 12,000 gallons per month per household, plus a 39% groundwater recharge credit based upon our water purchase from AVEK.  The Board of Directors will be discussing a water rate adjustment to meet the increasing costs to pump and purchase water.  Current Rates, as of April 1, 2023, are:

Water Charges 	$ 55.00 base rate which includes water use up to 20,000 gallons

$  2.50 per thousand gallons between 21,000 and 100,000 gallons

$  2.70 per thousand gallons over 100,000 gallons usage

Standby Charges	$ 20.00 per parcel each month

There are no special water rates for agricultural use or special circumstances. All shareholders are billed equally based upon their water use. If you are having trouble paying your bill, the Board may consider, on a case by case basis, accepting payments over time on delinquent accounts. All payment arrangements must include monthly payment of all current charges in addition to payment in full of the delinquency within 6 months.  If you default on your payment agreement, water service will be shut off with no further notice. If water service has been shut off due to delinquency, payment in full of all charges, including shut off/turn on fees, must be paid prior to reinstatement of water service.

All payments must be mailed to Sunnyside Farms Mutual Water Company, Post Office Box 901025. Palmdale, CA 95590, to arrive by the end of the month in which the invoice has been received. Late fees are assessed on accounts unpaid after 25 days. Payments must be made by check, money order or bill pay via your financial institution. Credits Cards or phone payments are not accepted. There is no drop off point for payments at this time. Please include your account number on your payment to ensure proper credit to your account. We are beta-testing the use of Zelle as an electronic payment method. If you are interested in paying via Zelle, send email to ssfmwc@gmail.com requesting instructions.

Sunnyside Farms Mutual Water Company delivers water which meets or exceeds public health standards for potable water.  Consumer contact information must be kept current with the Water Company office for notification in case of emergency.        We do not share personal consumer information with any other Agency.

All active accounts are required to have a gate valve installed on the property side of the water meter. This gate valve is for the convenience of the home owner when making plumbing repairs or any time you need the water shut off to your property. If you need the water turned off at the water meter, please call Morrison Well Maintenance at 661-466-6031. After hours emergency shut offs will be billed to the property owner. If the water meter valve is broken by anyone other than Sunnyside Farms MWC Maintenance personnel, the cost for repair or replacement will be billed to the property owner.

Even with the recent rains, the drought condition in the State of California is long term. The State has set a goal of no more than 55,000 gallons of water per residence by 2030. All consumers are asked to exercise conservation measures in order to avoid the imposition of water restrictions and penalties by State or County Agencies.  Check your sprinkler systems and evaporative coolers for leaks regularly and remain aware of your consumption.   **   PLEASE USE WATER WISELY  **

More information on water conservation in California can be found at:

https://www.watereducation.org/post/water-conservation-tips