## 2021 Consumer Confidence Report

|  |  |  |  |
| --- | --- | --- | --- |
| Water System Name: | **El Dorado Mutual Water Company** | Report Date: | June 4, 2022 |

*We test the drinking water quality for many constituents as required by state and federal regulations. This report shows the results of our monitoring for the period of January 1 to December 31, 2021 and may include earlier and more recent monitoring data.*

**Este informe contiene información muy importante sobre su agua para beber. Favor de comunicarse State Water Resources Control Board / Division of Drinking Water a (818) 551-2055 para asistencia en español. This Report Statement can be obtained, translated into Five Non-English Languages (Spanish, Mandarin, Tagalog, Vietnamese, and Hmong) via the State Water Resources Control Board https://www.waterboards.ca.gov**

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Type of water source(s) in use: | | Ground-Water and Treated Surface Water as a secondary source of supply | | | | | |
| Name & general location of source(s): | | | Community ground-water well and California Aqueduct water purchased from | | | | |
| Antelope Valley East Kern Water Agency (AVEK) | | | | | | | |
| Drinking Water Source Assessment information: | | | | Ground-water is vulnerable to nitrates from septic tanks and fertilizer use. | | | |
| Water storage tanks may be vulnerable to contamination. | | | | | | | |
| Time and place of regularly scheduled board meetings for public participation: | | | | | Board Meetings, held on the fourth | | |
| Tuesday of each month, are open to Shareholders and Residents with advance notification. | | | | | | | |
| For more information, contact: | Jeanne Miller via [eldmwc@gmail.com](mailto:eldmwc@gmail.com) or | | | | | Phone: | (661) 947-3255 |

|  |  |
| --- | --- |
| **TERMS USED IN THIS REPORT** | |
| **Maximum Contaminant Level (MCL)**: The highest level of a contaminant that is allowed in drinking water. Primary MCLs are set as close to the PHGs (or MCLGs) as is economically and technologically feasible. Secondary MCLs are set to protect the odor, taste, and appearance of drinking water.  **Maximum Contaminant Level Goal (MCLG)**: The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs are set by the U.S. Environmental Protection Agency (U.S. EPA).  **Public Health Goal (PHG)**: The level of a contaminant in drinking water below which there is no known or expected risk to health. PHGs are set by the California Environmental Protection Agency.  **Maximum Residual Disinfectant Level (MRDL)**: The highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.  **Maximum Residual Disinfectant Level Goal (MRDLG)**:The level of a drinking water disinfectant below which there is no known or expected risk to health. MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants.  **Primary Drinking Water Standards (PDWS)**: MCLs and MRDLs for contaminants that affect health along with their monitoring and reporting requirements, and water treatment requirements. | **Secondary Drinking Water Standards (SDWS)**:MCLs for contaminants that affect taste, odor, or appearance of the drinking water. Contaminants with SDWSs do not affect the health at the MCL levels.  **Treatment Technique (TT)**: A required process intended to reduce the level of a contaminant in drinking water.  **Regulatory Action Level (AL)**: The concentration of a contaminant which, if exceeded, triggers treatment or other requirements that a water system must follow.  **Variances and Exemptions**: Permissions from the State Water Resources Control Board (State Board) to exceed an MCL or not comply with a treatment technique under certain conditions.  **Level 1 Assessment**: A Level 1 assessment is a study of the water system to identify potential problems and determine (if possible) why total coliform bacteria have been found in our water system.  **Level 2 Assessment**: A Level 2 assessment is a very detailed study of the water system to identify potential problems and determine (if possible) why an *E. coli* MCL violation has occurred and/or why total coliform bacteria have been found in our water system on multiple occasions.  **ND**: not detectable at testing limit **ppm**: parts per million or milligrams per liter (mg/L) **ppb**: parts per billion or micrograms per liter (µg/L) **ppt**: parts per trillion or nanograms per liter (ng/L)  **ppq**: parts per quadrillion or picogram per liter (pg/L) **pCi/L**: picocuries per liter (a measure of radiation) |

**The sources of drinking water** (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells. As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.

**Contaminants that may be present in source water include:**

* *Microbial contaminants*, such as viruses and bacteria, that may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.
* *Inorganic contaminants*, such as salts and metals, that can be naturally-occurring or result from urban stormwater runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.
* *Pesticides and herbicides*, that may come from a variety of sources such as agriculture, stormwater runoff, and residential uses.
* *Organic chemical contaminants*, including synthetic and volatile organic chemicals, that are byproducts of industrial processes and petroleum production, and can also come from gas stations, storm-water runoff, agricultural application, and septic systems.
* *Radioactive contaminants*, that can be naturally-occurring or be the result of oil and gas production and mining activities.

**In order to ensure that tap water is safe to drink**, the U.S. EPA and the State Board prescribe regulations that limit the amount of certain contaminants in water provided by public water systems. The U.S. Food and Drug Administration regulations and California law also establish limits for contaminants in bottled water that provide the same protection for public health.

**The Tables below list all of the drinking water contaminants that were detected during the most recent sampling for the constituent**. The presence of these contaminants in the water does not necessarily indicate that the water poses a health risk. The State Board allows us to monitor for certain contaminants less than once per year because the concentrations of these contaminants do not change frequently. Some of the data, though representative of the water quality, are more than one year old. Any violation of an AL, MCL, MRDL, or TT is asterisked. Additional information regarding the violation is provided later in this report.

|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Table 1 – SAMPLING RESULTS SHOWING the detection of coliform bacteria | | | | | | | | | | | | |
| **Microbiological Contaminants** (complete if bacteria detected) | | **Highest No. of Detections** | | **No. of Months in Violation** | | MCL | | | | | **MCLG** | **Typical Source of Bacteria** |
| Total Coliform Bacteria (state Total Coliform Rule) | | (0) | | 0 | | 1 positive monthly sample (a) | | | | | 0 | Naturally present in the environment |
| Fecal Coliform or *E. coli* (state Total Coliform Rule) | | (0) | | 0 | | A routine sample and a repeat sample are total coliform positive, and one of these is also fecal coliform or *E. coli* positive | | | | | 0 | Human and animal fecal waste |
| *E. coli*  (federal Revised Total Coliform Rule) | | (0) | | 0 | | (b) | | | | | 0 | Human and animal fecal waste |
| (a) Two or more positive monthly samples is a violation of the MCL  (b) Routine and repeat samples are total coliform-positive and either is *E. coli*-positive or system fails to take repeat samples following *E. coli*-positive routine sample or system fails to analyze total coliform-positive repeat sample for *E. coli*. | | | | | | | | | | | | |
| Table 2 – SAMPLING RESULTS SHOWING THE detection of Lead and copper | | | | | | | | | | | | |
| Lead and Copper (complete if lead or copper detected in the last sample set) | **Sample Date** | | **No. of Samples Collected** | | **90th Percentile Level Detected** | | **No. Sites Exceeding AL** | **AL** | **PHG** | **No. of Schools Requesting Lead Sampling** | | **Typical Source of Contaminant** |
| Lead (ppb) | 8-25-20 | | 10 | | ND | | 0 | 15 | 0.2 | Not Applicable | | Internal corrosion of household water plumbing systems; erosion of natural deposits |
| Copper (ppm) | 8-25-20 | | 10 | | .17 mg/L | | 0 | 1.3 | 0.3 | Not Applicable | | Internal corrosion of household plumbing systems; erosion of natural deposits. |

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| TAble 3 – SAMPLING RESULTS FOR sodium and hardness | | | | | | | |
| **Chemical or Constituent** (and reporting units) | **Sample Source** | | **Level Detected** | **Range of Detections** | **MCL** | **PHG (MCLG)** | **Typical Source of Contaminant** |
| Sodium (ppm)  Sampled 3-9-22 | AVEK  Well | | 60  110 |  | None | None | Salt present in the water and is generally naturally occurring |
| Hardness (ppm)  Sampled 3-9-22 | AVEK  Well | | 74  290 |  | None | None | Sum of polyvalent cations present in the water, generally magnesium and calcium, and are usually naturally occurring |
| **TAble 4 – detection of contaminants with a Primary Drinking Water Standard** | | | | | | | |
| **Chemical or Constituent** (and reporting units) | | **Sample Source** | **Level Detected** | **Range of Detections** | **MCL [MRDL]** | **PHG (MCLG) [MRDLG]** | **Typical Source of Contaminant** |
| Barium ug/L  Sampled 3-9-22 | | AVEK  Well | ND  100 |  | 1000 | 2000 | Discharge from metal refineries; erosion of natural deposits |
| Bromate ug/L | | AVEK | 1.7 | 0.8-2.2 | 10 | 0.1 | By-product of drinking water disinfection |
| Chlorine mg/L | | AVEK | 1.11 | 1.09-1.12 | 4.0 | 4.0 | By-product of drinking water disinfection |
| Copper ug/L  Well sampled 3-9-22 | | AVEK  Well | ND  60 |  | 1000 | 170 | Erosion from natural deposits |
| Fluoride mg/L  Sampled 3-9-22 | | AVEK  Well | 0.07  0.23 |  | 2 | 1 | Erosion of natural deposits; discharge from fertilizer factories |
| Lead ug/L  Sampled 3-9-22 | | Well | 1.1 |  | 15 | .02 | Erosion of natural deposits; plumbing corrosion |
| Nitrate (as N) mg/L  Sampled 2/9/21 &  3-9-22 | | AVEK  Well | < 1  1.2 | 0.85  1.1-1.3 | 10 | 10 | Run off or leaching from fertilizer; leaching from septic tanks; erosion of natural deposits |
| Total Trihalomethanes ug/L Sampled 7-7-21 | | AVEK  System | 24  1.2 | 18-45  ND-15 | 80 | N/A | By-product of drinking water disinfection |
| Haloacetic Acids ug/L  Sampled 7-7-21 | | AVEK  System | 4.9  ND | ND-8.5  ND | 60 | N/A | By-product of drinking water disinfection |
| Uranium pCi/L | | AVEK  Well | 6.0  7 | 4.8-6.9 | 20 |  | Erosion of natural deposits |
| Gross Alpha pCi/L | | AVEK  Well | 5.3  9.3 | ND-9.4 | 15 | N/A | Erosion of natural deposits |
| **TAble 5 – detection of contaminants with a Secondary Drinking Water Standard**  There are no PHGs, MCLGs for these constituents because secondary MCLs are set on the basis of aesthetics. | | | | | | | |
| **Chemical or Constituent** (and reporting units) | | **Sample Source** | **Level Detected** | **Range of Detections** | **SMCL** | **PHG (MCLG)** | Typical Source of Contaminant |
| Chloride mg/L  Sampled 3-9-22 | | AVEK  Well | 59  74 |  | 500 | N/A | Run-off/leaching from natural deposits |
| Sulfate mg/L  Sampled 3-9-22 | | AVEK  Well | 74  190 |  | 250 | N/A | Run-off/leaching from natural deposits |
| Total Organic Carbon mg/L | | AVEK | 1.8 | 1.3-2.4 | N/A | N/A | Water Treatment Technique; natural sources |
| Specific Conductance umhos 3-9-22 | | AVEK  Well | 480  1100 | 470-480 | 1600 | N/A | Substances that for ions when in water |
| Total Dissolved Solids mg/L 3-9-33 | | AVEK  Well | 280  650 |  | 1000 | N/A | Run-off/leaching from natural deposits |
| Turbidity units  Sampled 3-9-22 | | AVEK  Well | < 1  0.11 | 0.02-0.11 | 5 | N/A | Soil Run-off |
| Zinc ug/L  Sampled 3-8-22 | | AVEK  Well | 650  59 |  | 5000 | N/A | Run-off/leaching from natural deposits; industrial wastes |
| **TAble 6 – detection of UNREGULATED CONTAMINANTS** | | | | | | | |
| **Chemical or Constituent** (and reporting units) | | **Sample Source** | **Level Detected** | **Range of Detections** | **Notification Level** | | **Informational data for Consumers** |
| Calcium mg/L  Sampled 3-9-22 | | AVEK  Well | 26  87 |  | No Standard | | Leaching/erosion from natural deposits |
| Magnesium mg/L  Sampled 3-9-22 | | AVEK  Well | 2.3  18 |  | No Standard | | Leaching/erosion from natural deposits |
| Potassium mg/L  Sampled 3-9-22 | | Well | 3.1 |  | No Standard | | Leaching/erosion from natural deposits |
| pH units  Sampled 3-9-22 | | AVEK  Well | 7.2  7.9 | 7.0-7.5 | No Standard | | The acidity or alkalinity of water on a scale on which 7 is neutral, lower = more acid and higher = more alkaline. |
| Bicarbonate Alkalinity as HCO3 mg/L 3-9-22 | | AVEK  Well | 120  230 |  | No Standard | | Aids in neutralizing the acids in water, therefore helping to balance the pH |
| Total Alkalinity mg/L  Sampled 3-9-22 | | AVEK  Well | 96  230 |  | No Standard | | Indicative of the water’s ability to neutralize acid. |

**Additional General Information on Drinking Water**

Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants. The presence of contaminants does not necessarily indicate that the water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the U.S. EPA’s Safe Drinking Water Hotline (1-800-426-4791).

Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care providers. U.S. EPA/Centers for Disease Control (CDC) guidelines on appropriate means to lessen the risk of infection by *Cryptosporidium* and other microbial contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791). If you are concerned about lead in your water, you may wish to have your water tested. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline (1-800-426-4791) or at <http://www.epa.gov/lead>.

**During 2021 the water in our distribution system was a blend of AVEK water and ground-water on multiple occasions, therefore we have included the AVEK test results in this report. More information on AVEK’s water can** **be found at** [**www.avek.org**](http://www.avek.org)**. The laboratory results from our water testing are available for review by appointment at the El Dorado Mutual Water Company office. We will use AVEK water again during 2022 while wellsite upgrades are under construction. If you have questions regarding the water quality testing process, contact Mark Williams at 661-435-7165.**

**El Dorado Mutual Water Company delivers water which meets or exceeds public health standards for potable water. Due to the Antelope Valley ground-water adjudication and State water conservation mandates, ground-water management remains a top priority. Consumer contact information must be kept current with the Water Company office in case of emergency. We do not share personal consumer information with any other Agency. El Dorado MWC does not store or provide account information on the internet therefore your personal information is not subject to compromise.**

**All active accounts are required to have a gate valve installed on the property side of the water meter. This gate valve is for the convenience of the home owner when making plumbing repairs or any time you need the water shut off to your property. If you need the water turned off at the water meter, please call Mark Williams at 661-435-7165. After hours emergency shut offs will be billed to the property owner. If the water meter valve is broken by anyone other than El Dorado MWC maintenance personnel, the cost for repair or replacement will be billed to the property owner. Water meters must be accessible to maintenance personnel at all times. No fencing may be erected which impedes access to the water meter or water lines in the road easements. Road/Utility Easements must be kept free from obstruction. Property owners are responsible for the maintenance of their easements. Do not use tractors or heavy equipment near or on the edge of the roads as that can cause damage to the road. Our private roads were designed for normal rural residential use. Any property owner causing excessive wear and/or damage to the Private Roads will be billed directly for the cost of the specific road repair. A $500 fine will be assessed for abandoned appliances, furniture, building materials, debris and trash left for over 7 days on the Water Company and Road Easements. Property owners will also be billed the cost for the removal of debris and easement obstructions.**

**Local law enforcement has asked the public to report unauthorized use of fire hydrants. Please contact the El Dorado MWC office if you observe anyone accessing our private hydrants. There is a $500 fine for unauthorized hydrant use.**

**The State of California has notified all Agencies that the ongoing drought is expected to worsen. All consumers are asked to reduce water consumption by at least 15%. Please exercise conservation measures in order to avoid the imposition of water restrictions and penalties by the State or Local Authorities. Check your sprinkler systems and evaporative coolers for leaks on a regular basis and remain aware of your consumption.**

**More information on California’s water conservation mandates and helpful tips can be found at:**

[**https://www.watereducation.org/post/water-conservation-tips**](https://www.watereducation.org/post/water-conservation-tips)

**As a not for profit, mutual benefit corporation, El Dorado Mutual Water does not have access to funds in order to offer any incentives for your water conservation efforts, however the Antelope Valley Resource Conservation district is offering a lawn reduction rebate program. You can contact them at 661-942-7306 or check out their website for details.**

[**https://www.avrcd.org/grass-reduction-program**](https://www.avrcd.org/grass-reduction-program)

**PLEASE USE WATER WISELY**