# 2024 Consumer Confidence Report

## Water System Information

**Water System Name:** Whale Gulch School

**Report Date:** 6/24/2025.

**Type of Water Source(s) in Use:** Surface Water

**Name and General Location of Source(s):** Syreeta Creek, located east of the school.

**Drinking Water Source Assessment Information:** There has been no source water assessment conducted on Syreeta Creek

**Time and Place of Regularly Scheduled Board Meetings for Public Participation:** The 2nd Wednesday of every month at 4:00pm. Location alternates every month from Whale Gulch School or Leggett Unified School

**For More Information, Contact:** Brenda Bullington at (707) 986-7131.

## About This Report

We test the drinking water quality for many constituents as required by state and federal regulations. This report shows the results of our monitoring for the period of January 1 to December 31, 2024, and may include earlier monitoring data.

## Importance of This Report Statement in Spanish

Language in Spanish: Este informe contiene información muy importante sobre su agua para beber. Favor de comunicarse Whale Gulch School a (707) 986-7131 para asistirlo en español.

## Terms Used in This Report

| **Term** | **Definition** |
| --- | --- |
| Level 1 Assessment | A Level 1 assessment is a study of the water system to identify potential problems and determine (if possible) why total coliform bacteria have been found in our water system. |
| Level 2 Assessment | A Level 2 assessment is a very detailed study of the water system to identify potential problems and determine (if possible) why an *E. coli* MCL violation has occurred and/or why total coliform bacteria have been found in our water system on multiple occasions. |
| Maximum Contaminant Level (MCL) | The highest level of a contaminant that is allowed in drinking water. Primary MCLs are set as close to the PHGs (or MCLGs) as is economically and technologically feasible. Secondary MCLs are set to protect the odor, taste, and appearance of drinking water. |
| Maximum Contaminant Level Goal (MCLG) | The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs are set by the U.S. Environmental Protection Agency (U.S. EPA). |
| Maximum Residual Disinfectant Level (MRDL) | The highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants. |
| Maximum Residual Disinfectant Level Goal (MRDLG) | The level of a drinking water disinfectant below which there is no known or expected risk to health. MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants. |
| Primary Drinking Water Standards (PDWS) | MCLs and MRDLs for contaminants that affect health along with their monitoring and reporting requirements, and water treatment requirements. |
| Public Health Goal(PHG) | The level of a contaminant in drinking water below which there is no known or expected risk to health. PHGs are set by the California Environmental Protection Agency. |
| Regulatory Action Level(AL) | The concentration of a contaminant which, if exceeded, triggers treatment or other requirements that a water system must follow. |
| Secondary Drinking Water Standards (SDWS) | MCLs for contaminants that affect taste, odor, or appearance of the drinking water. Contaminants with SDWSs do not affect the health at the MCL levels. |
| Treatment Technique(TT) | A required process intended to reduce the level of a contaminant in drinking water. |
| Variances and Exemptions | Permissions from the State Water Resources Control Board (State Board) to exceed an MCL or not comply with a treatment technique under certain conditions. |
| ND | Not detectable at testing limit. |
| ppm | parts per million or milligrams per liter (mg/L) |
| ppb | parts per billion or micrograms per liter (µg/L) |
| ppt | parts per trillion or nanograms per liter (ng/L) |
| ppq | parts per quadrillion or picogram per liter (pg/L) |
| pCi/L | picocuries per liter (a measure of radiation) |

## Sources of Drinking Water and Contaminants that May Be Present in Source Water

The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells. As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.

Contaminants that may be present in source water include:

* Microbial contaminants, such as viruses and bacteria, that may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.
* Inorganic contaminants, such as salts and metals, that can be naturally-occurring or result from urban stormwater runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.
* Pesticides and herbicides, that may come from a variety of sources such as agriculture, urban stormwater runoff, and residential uses.
* Organic chemical contaminants, including synthetic and volatile organic chemicals, that are byproducts of industrial processes and petroleum production, and can also come from gas stations, urban stormwater runoff, agricultural application, and septic systems.
* Radioactive contaminants, that can be naturally-occurring or be the result of oil and gas production and mining activities.

## Regulation of Drinking Water and Bottled Water Quality

In order to ensure that tap water is safe to drink, the U.S. EPA and the State Board prescribe regulations that limit the amount of certain contaminants in water provided by public water systems. The U.S. Food and Drug Administration regulations and California law also establish limits for contaminants in bottled water that provide the same protection for public health.

## About Your Drinking Water Quality

### Drinking Water Contaminants Detected

Tables 1, 2, 3, 4, 5, 6, and 8 list all of the drinking water contaminants that were detected during the most recent sampling for the constituent. The presence of these contaminants in the water does not necessarily indicate that the water poses a health risk. The State Board allows us to monitor for certain contaminants less than once per year because the concentrations of these contaminants do not change frequently. Some of the data, though representative of the water quality, are more than one year old. Any violation of an AL, MCL, MRDL, or TT is asterisked. Additional information regarding the violation is provided later in this report.

Table . Sampling Results Showing the Detection of Coliform Bacteria

| **Microbiological Contaminants** | **Highest No. of****Detections** | **No. of Months in Violation** | **MCL** | **MCLG** | **Typical Source of Bacteria** |
| --- | --- | --- | --- | --- | --- |
| *E. coli* | 0 | 0 | 0 | 0 | Human and animal fecal waste |

Routine and repeat samples are total coliform-positive and either is *E. coli*-positive or system fails to take repeat samples following *E. coli*-positive routine sample or system fails to analyze total coliform-positive repeat sample for *E. coli*.

Table . Sampling Results Showing the Detection of Lead and Copper

| **Lead and****Copper** | **Sample Date** | **# of Samples****Collected** | **90th Percentile Level Detected** | **# Sites****Exceeding AL** | **AL** | **PHG** | **Typical Source of****Contaminant** |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Lead (ppb) | 2023 | 5 | 0 | 0 | 15 | 0.2 | Internal corrosion of household water plumbing systems; discharges from industrial manufacturers; erosion of natural deposits |
| Copper (ppm) | 2023 | 5 | 0.2 | 0 | 1.3 | 0.3 | Internal corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives |

Table . Sampling Results for Sodium and Hardness

| **Chemical or****Constituent****(& reporting units)** | **Sample Date** | **Level****Detected** | **Range of Detections** | **MCL** | **PHG (MCLG)** | **Typical Source of Contaminant** |
| --- | --- | --- | --- | --- | --- | --- |
| Sodium (ppm) | 2017 | 17 | n/a | None | None | Salt present in the water and is generally naturally occurring |
| Hardness (ppm) | 2019 | 8.8 | n/a | None | None | Sum of polyvalent cations present in the water, generally magnesium and calcium, and are usually naturally occurring |

Table . Detection of Contaminants with a Primary Drinking Water Standard

| **Chemical or****Constituent****(& reporting units)** | **Sample Date** | **Level****Detected** | **Range of****Detections** | **MCL [MRDL]** | **PHG (MCLG) [MRDLG]** | **Typical Source of****Contaminant** |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Barium (mg/L) | 10/10/24 | 0.012 | n/a | 1 | 2 | Some people who drink water containing barium in excess of the MCL over many years may experience an increase in blood pressure. |  |  |  |  |
| Nitrate (mg/L) | 10/10/24 | 0.17 (as N) | n/a | 10(as N) | 10(as N) | Infants below the age of six months who drink water containing nitrate in excess of the MCL may quickly become seriously ill and, if untreated, may die because high nitrate levels can interfere with the capacity of the infant’s blood to carry oxygen. Symptoms include shortness of breath and blueness of the skin. High nitrate levels may also affect the oxygen-carrying ability of the blood of pregnant women. |  |  |  |  |
| TTHMs (total Trihalomethanes)(ug/l) | 2024 | 31 | n/a | 80 | n/a | Some people who drink water containing trihalomethanes ins excess of the MCL over years may experience liver, kidney, or central nervous system problems, and may have an increased risk of getting cancer. |  |  |  |  |

Table . Detection of Contaminants with a Secondary Drinking Water Standard

|  |
| --- |
| According to 22CCR 64449 (g) Non transient – non community water systems (NTNCWS) shall monitor their sources of distribution system entry points representative of the effluent for secondary drinking water standards at least once. As NTNCWS, Whale Gulch School has been required to test for contaminants with a secondary drinking water standard in the past nine years |

Table . Detection of Unregulated Contaminants

|  |
| --- |
| The Safe Drinking Water Act requires that once every five years, the Environmental Protection Agency (EPA) issue a list of priority unregulated contaminants to be monitored by certain public water systems across States, Tribes, and Territories. For more information on unregulated contaminants, you can visit the EPA website -Monitoring Unregulated Contaminates in Drinking Water, US EPAAS a water system serving less than 3,300 people, Whale Gulch School is not required to sample for Unregulated Contaminants |

### Additional General Information on Drinking Water

Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants. The presence of contaminants does not necessarily indicate that the water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the U.S. EPA’s Safe Drinking Water Hotline (1-800-426-4791).

Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care providers. U.S. EPA/Centers for Disease Control (CDC) guidelines on appropriate means to lessen the risk of infection by *Cryptosporidium* and other microbial contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791).

Lead-Specific Language: If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children. Lead in drinking water is primarily from materials and components associated with service lines and home plumbing. Whale Gulch School is responsible for providing high quality drinking water but cannot control the variety of materials used in plumbing components. When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to 2 minutes before using water for drinking or cooking. If you do so, you may wish to collect the flushed water and reuse it for another beneficial purpose, such as watering plants. If you are concerned about lead in your water, you may wish to have your water tested. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline (1-800-426-4791) or at <http://www.epa.gov/lead>.

#### Summary Information for Violation of a MCL, MRDL, AL, TT, or Monitoring and Reporting Requirement

Table 7. Violation of a MCL, MRDL, AL, TT or Monitoring Reporting Requirement

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| Violation  | Explanation | Duration | Actions Taken to Correct Violation | Health Effects Language |
| Whale Gulch School has no violations of a MCL, MRDL, AL, TT, or monitoring reporting requirement to report for 2024. |

#### for Water Systems Providing Groundwater as a Source of Drinking Water.

#### **Table 8 & Table 9 are for groundwater systems and do not apply to Whale Gulch School. they have been deleted from this report.**

#### For Systems Providing Surface Water as a Source of Drinking Water

Table 10. Sampling Results Showing Treatment of Surface Water Sources

|  |  |
| --- | --- |
| Treatment Technique (a) (Type of approved filtration technology used) | Harmasco Municipal Filter System |
| Turbidity Performance Standards (b) (that must be met through the water treatment process) | Turbidity of the filtered water must:1 – Be less than or equal to 0.3 NTU in 95% of measurements in a month2 – Not exceed [1.0 NTU for more than eight consecutive hours.3 – Not exceed 1.0 NTU at any time |
| Lowest monthly percentage of samples that met Turbidity Performance Standard No. 1. | 100% were less than or equal to 0.3 NTU. |
| Highest single turbidity measurement during the year | 0.045  |
| Number of violations of any surface water treatment requirements | 0 |

(a) A required process intended to reduce the level of contaminants in drinking water.

(b) Turbidity (measured in NTU) is a measurement of the cloudiness of water and is a good indicator of water quality and filtration performance. Turbidity results which meet performance standards are considered to be in compliance with filtration requirements.

#### Summary Information for Violation of a Surface Water TT

Table 11. Violation of Surface Water TT

|  |
| --- |
| Whale Gulch School has no violations of surface Water TT to report in 2024 |

#### Summary Information for Operating Under a Variance or Exemption

Whale Gulch School did not operate under a variance or exemption for 2024.

#### Summary Information for Revised Total Coliform Rule Level 1 and Level 2 Assessment Requirements

Whale Gulch School was not required to conduct a level 1 or level 2 assessment related to the revised coliform rule in 2024.