# 2024 Consumer Confidence Report

## Water System Information

Water System Name: Golden Era Productions Water System CA3301280

Report Date: 23 June 2025

Type of Water Source(s) in Use: Groundwater pumped from Golden Era’s two wells.

Name and General Location of Source(s): The water system currently consists of two active wells – Well 1 and Well 2.

## Well 1 located in the south center of the facility was drilled in 1989 and is 810 feet deep with 805 feet of 14” steel casing. The well has a 150 HP vertical turbine pump. This well is the main source of our Drinking water. The water from this well is pumped up to the Reservoir on the north side of the property 212’ above the well.

## Well 2 is located in the southwest corner of the property. It was drilled in 1989 and is 835 feet deep. The vertical turbine pump is driven by a 350 HP motor. Well 2 is primarily used for irrigation but is a back-up drinking water source should Well 1 be off line.

Time and Place of Regularly Scheduled Board Meetings for Public Participation: This is a private facility with a daily newsletter and notice boards. Briefings are made on state of wells, ground water levels and impact of rainfall on our water system.

For More Information, Contact: Kathleen Riordan, Licenses D2 50098 and T2 43223

Phone: (951) 487-7200 or internal extension 490.

## About This Report

We test the drinking water quality for many constituents as required by state and federal regulations.  This report shows the results of our monitoring for the period of January 1 to December 31, 2024 and may include earlier monitoring data. The report contains specific language and data as required by state and federal regulations which have been indicated in blue type.

Terms Used in This Report

| Term | Definition |
| --- | --- |
| Level 1 Assessment | A Level 1 assessment is a study of the water system should the need arise to identify potential problems and determine (if possible) why total coliform bacteria have been found. |
| Level 2 Assessment | A Level 2 assessment is a very detailed study of the water system to identify potential problems and determine (if possible) why an E. coli Maximum Contaminant Level (MCL) violation has occurred and/or why total coliform bacteria have been found in a water system on multiple occasions. |
| Maximum Contaminant Level (MCL) | The highest level of a contaminant that is allowed in drinking water. Primary Maximum Contaminant Levels (those related to health) are set as close to the Public Health Goals (or Maximum Contaminant Level Goal -- MCLGs) as are economically and technologically feasible. Secondary Maximum Contaminant Levels (SMCLs) are set by the Environmental Protection Agency to protect the aesthetics (odor, taste, and appearance of drinking water). California has taken the EPA Secondary standards and incorporated them into a law and so if any of the items listed as affecting color, odor and taste exceed the limits, action will need to be taken to reduce the levels. |
| Maximum Contaminant Level Goal (MCLG) | The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs are set by the U.S. Environmental Protection Agency (U.S. EPA). |
| Maximum Residual Disinfectant Level (MRDL) | The highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants. |
| Maximum Residual Disinfectant Level Goal (MRDLG) | The level of a drinking water disinfectant below which there is no known or expected risk to health. MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants. |
| Primary Drinking Water Standards (PDWS) | These are the Maximum Contaminant Levels (MCLs) and Maximum Residual Disinfectant Levels (MRDLs) as established by the Environmental Protection Agency and enforced by the California State Water Board for contaminants that affect health. Included are the monitoring and reporting requirements, and water treatment requirements. |
| Public Health Goal (PHG) | The level of a contaminant in drinking water below which there is no known or expected risk to health. PHGs are set by the California Environmental Protection Agency. |
| Regulatory Action Level (AL) | The concentration of a contaminant which, if exceeded, triggers treatment or other requirements that a water system must follow. |
| Secondary Drinking Water Standards (SDWS) | MCLs for contaminants that affect taste, odor, or appearance of the drinking water. These are set by the US Environmental Protection Agency. In California, however, some of these contaminants that exceed the maximum limit are required by California law to be treated such as water filtration for the removal of iron and manganese in drinking water. Contaminants with Secondary Drinking Water Standards (SDWS) do not affect health at the MCL levels. |
| Treatment Technique (TT) | A required process intended to reduce the level of a contaminant in drinking water. |
| Variances and Exemptions | Permissions from the State Water Resources Control Board to exceed an MCL or not comply with a treatment technique under certain conditions. |
| ND | Not detectable at testing limit. |
| ppm | parts per million or milligrams per liter (mg/L) As a comparative: 1 part per million is equivalent to: 1 second in a span of 11.5 days 1 teaspoon in 1,302 gallons |
| ppb | parts per billion or micrograms per liter (µg/L) As a comparative: 1 part per billion is equivalent to: 1 second in nearly 32 years or 1 teaspoon in 1.3 million gallons |
| ppt | parts per trillion or nanograms per liter (ng/L) As a comparative: 1 part per trillion is equivalent to: 1 second in nearly 32,000 years 1 teaspoon in 1.3 billion gallons |
| ppq | parts per quadrillion or picogram per liter (pg/L) |
| pCi/L | picocuries per liter (a curie is a measure of radiation and a picocurie is one trillionth of a curie) |
| Threshold of Odor Unit (TON) | A measurement of the lowest concentration of certain compounds perceivable by the human sense of smell |
| Turbidity Measurement (NTU) | An NTU is a unit of measure using a special meter that measures water’s cloudiness. See photo. |

## Sources of Drinking Water and Contaminants that May Be Present in Source Water

Drinking water sources (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs and wells.

As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.

Well water which moves through the underground water-bearing layers of rock dissolves the naturally occurring mineral deposits such as calcium, magnesium, iron and manganese.

At Golden Era our drinking water is from wells. We monitor the water quality with monthly, quarterly and annual water testing using one of the largest accredited laboratories in the Riverside area. In 2024 our drinking water met all U.S. Environmental Protection Agency’s and State of California’s stringent drinking water health standards with results either zero or a small fraction of the established standards for drinking water.

Treatment

Our water is chlorinated not only to disinfect it but to improve taste and reduce color and odor.  By way of example, as this area had a volcanic history, the ground water has a sulfuric odor. Chlorination removes that odor.

Chlorine reacts with naturally occurring residues that seep into the underground water supply. Because these residues can be in groundwater we are required to test our water to determine whether any compounds have formed during the chlorination process. As these compounds, called disinfection byproducts, are regulated by the Environmental Protection Agency and the California State Water Board, we are obligated to test our water every three (3) years. The tests were done in 2023.

Our water was found to be either free of the compounds or showed two compounds that were ¼ of the maximum limit. The next set of tests required in 2026.

Contaminants

Various contaminants that may be present in source water which include:

Microbial contaminants, such as viruses and bacteria that may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.

Inorganic contaminants, such as salts and metals, that can be naturally-occurring or from urban stormwater runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.

Pesticides and herbicides that may come from a variety of sources such as agriculture, urban stormwater runoff, and residential uses.

Organic chemical contaminants, including synthetic and volatile organic chemicals that are byproducts of industrial processes and petroleum production, and can also come from gas stations, urban stormwater runoff, agricultural application, and septic systems.

Radioactive contaminants that can be naturally-occurring or can be the result of oil and gas production and mining activities.

## Regulation of Drinking Water and Bottled Water Quality

In order to ensure that tap water is safe to drink, the U.S. Environmental Protection Agency and the California State Water Board prescribe regulations limiting the levels of certain contaminants in water provided by public water systems.  Bottled water also falls under these same federal and state regulations.

## About Your Drinking Water Quality

### Drinking Water Contaminants Detected

Tables 1, 2, 3, 4, 5, 6, and 8 list all of the drinking water contaminants that were detected during the most recent sampling for that constituent.  The presence of these contaminants in the water does not necessarily indicate that the water poses a health risk.  The California State Board – Drinking Water Division allows us to test and monitor certain contaminants less than once per year because our concentrations are well below the limits and have not changed over the years.  Some of the data, though representative of the water quality, are more than one year old.  Any violation of an AL (Action Level), MCL (Maximum Contaminant Level), MRDL (Maximum Residual Disinfectant Level) or TT (Treatment Technique) is asterisked.  Additional information regarding the violation is provided later in this report.

Table 1.  Sampling Results Showing the Detection of Coliform Bacteria

Complete if bacteria are detected – None detected during 2024.

Table 2.  Sampling Results Showing the Detection of Lead and Copper

Complete if lead or copper is detected in the last sample set.

| Lead and Copper | Sample Date | No. of Samples Collected | 90th Percentile Level Detected | No. Sites Exceeding AL | Action Level (AL) | PHG | No. of Schools Requesting Lead Sampling | Typical Source of Contaminant |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Lead (ppb ug/l) | 21 Sep 2022 | 10 | 6.1 | 0 | 15 | 0.2 | Not Applicable | Internal corrosion of household water plumbing systems; discharges from industrial manufacturers; erosion of natural deposits |
| Copper (ppm mg/l) | 21 Sep 2022 | 10 | .86 | 0 | 1.3 mg/l | 0.3 | Not applicable | Internal corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives |

Table 3.  Sampling Results for Sodium and Hardness

| Chemical or Constituent (and reporting units) | Sample Date | Level Detected | Range of Detections | MCL | PHG (MCLG) | Typical Source of Contaminant |
| --- | --- | --- | --- | --- | --- | --- |
| Sodium (ppm or mg/l) | 26-Jan-2024 | 40 | 43 | None | None | Salt present in the water and is generally naturally occurring |
| Hardness (ppm or mg/l) | 26-Jan-2024 | 110 | 104 | None | None | Sum of positive charged ions present in the water, generally magnesium and calcium, and are usually naturally occurring |

Table 4.  Detection of Contaminants with a Primary Drinking Water Standard

| Chemical or Constituent (and reporting units) | Sample Date | Level Detected | Range of Detections | MCL [MRDL] | PHG (MCLG) [MRDLG] | Typical Source of Contaminant |
| --- | --- | --- | --- | --- | --- | --- |
| Fluoride in ppm (natural source only -- Golden Era does not treat its water with fluoride.) | 26-Jan-2024 | 0.68 ppm | 0.57 | 2 ppm | 1 ppm | Erosion of natural deposits; it is a water additive which promotes strong teeth; discharge from fertilizer and aluminum factories. |
| Barium (mg/L) | 26-Jan-2024 | 0.11 mg/L | 0.055 mg/L | 2 mg/L | 2 mg/L | Discharges of oil drilling wastes and from metal refineries; erosion of natural deposits Some people who drink water containing barium in excess of the MCL over many years may experience an increase in blood pressure. |
| Selenium (ug/L or ppb) | 26-Jan-2024 | 16 uG/L | 8 uG/L | 50 ug/L |  | Discharge from petroleum refineries; erosion of natural deposits; discharge from mines |
| Radium-228 (pico curies/L pCI/L) | 26-Jan-2024 | 0.585 +/-0.832 pCI/L | 0.2925 pCI/L | None set | 5 pCi/L | Erosion of natural deposits; |

Table 5.  Detection of Contaminants with a Secondary Drinking Water Standard

Monitoring required by section 64449 of the California Code of Regulations, Title 22. Secondary standards exceeding the Secondary Maximum Contaminant Level (SMCL) are highlighted. Iron and manganese, though listed by the EPA as a secondary contaminant affecting the aesthetic quality of the water, California does require monitoring as our water for manganese is above the secondary maximum contaminant limit noted in the Table below. Other secondary contaminants found in our water are noted.

| Chemical or Constituent (and reporting units) | Sample Date | Level Detected | Range of Detections | SMCL | Typical Source of Contaminant |
| --- | --- | --- | --- | --- | --- |
| Manganese (mg/L) | 26-Jan-2024 | 0.16 mg/L* | 0.155 mg/L | 0.05 mg/L | Leaching from natural deposits. Health Effects: High levels of manganese in people have been shown to result in adverse effects to the nervous system. |
| Color (Color Units) | 26-Jan-2024 | 20 mg/L | 17.5 mg/L | 15 | Naturally-occurring organic materials |
| Chloride mg/L | 26-Jan-2024 | 26 mg/L | 20.5 mg/L | 500 mg/l | Runoff/leaching from natural deposits; seawater (where applicable) |
| Turbidity (NTU) | 26-Jan-2024 | 4.5 | 2.34 NTU | 5 units | Soil runoff |
| Total Dissolved Solids (TDS) – mg/L | 26-Jan-2024 | 230 mg/L | 215 mg/L | 1000 mg/L | Runoff/leaching from natural deposits |
| Sulfate mg/L | 26-Jan-2024 | 2.6 mg/L | 1.3 mg/L | 500 mg/L | Runoff/leaching from natural deposits and/or industrial waste |

### For Water Systems Providing Groundwater as a Source of Drinking Water

| VIOLATION OF A MCL, MRDL, AL, TT, OR MONITORING AND REPORTING REQUIREMENT |  |  |  |  |
| --- | --- | --- | --- | --- |
| Violation | Explanation | Duration | Actions Taken to Correct the Violation | Health Effects Language |
| Manganese | Occurs with iron in the well water and is a Secondary Maximum Contaminant | Continual | Alert those consumers should there be instances of staining from the manganese in our laundry facilities, water softeners. | Health Effects: High levels of manganese in people have been shown to result in adverse effects to the nervous system. |
| Manganese is regulated by a 0.05 mg/L (ppm) secondary maximum contaminant level established to address aesthetic issues related to the discoloration of water. Manganese is a required nutrient with an intake range from 1.2 mg/day to 2.3 mg/day depending on the age of the user. Recent studies found that at high levels manganese can pose a nervous system risk. Our water has 0.16 mg/L of manganese which is above the 0.05 mg/L yet it is less than 0.5 mg/l – the level that may be a health concern. |  |  |  |  |

### Additional General Information on Drinking Water

Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that the water poses a health risk.  More information about contaminants and potential health effects can be obtained by calling the U.S. EPA’s Safe Drinking Water Hotline (1-800-426-4791).

Some people may be more vulnerable to contaminants in drinking water than the general population.  Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly and infants can be particularly at risk from infections.  These people should seek advice about drinking water from their health care providers.  U.S. EPA/Centers for Disease Control (CDC) guidelines on appropriate means to lessen the risk of infection by microbial contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791).

Lead-Specific Language:  If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children.  Lead in drinking water is primarily from materials and components associated with service lines and home plumbing.

Golden Era is responsible for providing high quality drinking water. As we replaced our plumbing over the years, our lead and copper tests show non-detection of any lead that has leached into the water from the plumbing.