A picture containing outdoor, sky, grass

Description automatically generated

2021 Consumer Confidence Report

idyllwild water district

**June 2022**

idyllwild water district

2021 Consumer Confidence Report



**Idyllwild Water District mission is to provide reliable water and sewer service in a safe, cost-effective, and environmentally sound manner in accordance with the community needs.**

**Board of Directors**

**Dr. Charles Schelly, President**

**Peter Szabadi, Vice President**

**Steve Kunkle, Director**

**Les Gin, Director**

**Steve Olson, Director**

**General Manager**

**Leo Havener**

**Chief Financial Officer**

**Hosny Shouman**

**Chief Water Operator**

**Joseph Reyes**

**Idyllwild Water District**

**25945 Hwy. 243**

**P.O. Box 397**

**Idyllwild, CA 92549**

**Phone (951) 659-2143**

**Fax (951) 659-9990**

The enclosed Consumer Confidence Report provides information regarding the quality of water that you received from the Idyllwild Water District (IWD) during 2021. IWD staff work diligently to provide its customers safe, high-quality water. We are required to monitor your drinking water for specific contaminants on a regular basis. Results of regular monitoring are an indicator of whether or not your drinking water meets health standards.

The District uses Foster Lake to recharge water naturally through percolating water, which maintains the groundwater levels to the surrounding Foster Lake wells. IWD receives water directly from Lilly Creek into Foster Lake. Our other source for Foster Lake is a stream diversion on Strawberry Creek that is pumped across town into the Lake. The current year (2021) produced about 80% of average snow and precipitation.

The Board of Directors and staff at the District are dedicated to preserving our watershed and sustaining our environment, now and into the future. Through cooperation and our customers continually improving efficiency in water use, IWD will create reliability of supply to cushion against extended future drought. Through community cooperation and the implementation of efficiencies, the Board of Directors strives to support the local economy and to ensure sustainable supplies for the future.

*We test the drinking water as required by state and federal regulations. This report shows the results of our monitoring for the period of January 1 - December 31, 2021 and may include earlier monitoring data.*

**Este informe contiene información muy importante sobre su agua para beber. Tradúzcalo ó hable con alguien que lo entienda bien. Favor de comunicarse Idyllwild Water District at (951) 659-2143.**

Type of water source(s) in use: Groundwater

Name & location of source(s): Water in 2021 was supplied from 12 of the 17 wells owned by IWD.

Drinking Water Source Assessment information: Completed in 2007 and is available for review at IWD office located at 25945 State Hwy. 243, Idyllwild, CA 92549.

Time & place of regularly scheduled Board meetings for public participation:

Third Wednesday of the month at 6:00 p.m. in the IWD Boardroom located at 25945 State Hwy. 243, Idyllwild, CA 92549. Information can be located on the district website, https://www.idyllwildwater.com.

For more information contact: Leo Havener, General Manager Phone: (951) 659-2143

**The sources of drinking water** (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells. As water travels over the surface of the land or through the ground, it dissolves naturally occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.

**Contaminants that may be present in source water include:**

* *Microbial contaminants*, such as viruses and bacteria that may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.
* *Inorganic contaminants*, such as salts and metals that can be naturally occurring or result from urban storm water runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.
* *Pesticides and herbicides* that may come from a variety of sources such as agriculture, urban storm water runoff, and residential uses.
* *Organic chemical contaminants*, including synthetic and volatile organic chemicals that are by-products of industrial processes and petroleum production, and can also come from gas stations, urban storm water runoff, agricultural application, and septic systems.
* *Radioactive contaminants* that can be naturally occurring or be the result of oil and gas production and mining activities.

**Regulation of Drinking Water and Bottled Water Quality**

In order to ensure that tap water is safe to drink, the U.S. Environmental Protection Agency (U.S. EPA) and the State Water Resources Control Board (State Board) prescribe regulations that limit the amount of certain contaminants in water provided by public water systems. The U.S. Food and Drug Administration regulations and State Board regulations also establish limits for contaminants in bottled water that provide the same protection for public health.

If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children. Lead in drinking water is primarily from materials and components associated with service lines and home plumbing. Idyllwild Water District is responsible for providing high quality drinking water but cannot control the variety of materials used in plumbing components.

When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to 2 minutes before using water for drinking or cooking. If you are concerned about lead in your water, you may wish to have your water tested. Infants and young children are typically more vulnerable to lead in drinking water than the general population. It is possible that lead levels at your home may be higher than at other homes in the community as a result of materials used in your home’s plumbing. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the U.S. EPA Safe Drinking Water Hotline (1-800-426-4791) or at http://www.epa.gov/safewater/lead.

**State Revised Total Coliform Rule (RTCR):** This Consumer Confidence Report (CCR) reflects changes in drinking water regulatory requirements during 2021. These revisions add the requirements of the federal Revised Total Coliform Rule, effective since April 1, 2016, to the existing state Total Coliform Rule. The revised rule maintains the purpose to protect public health by ensuring the integrity of the drinking water distribution system and monitoring for the presence of microbials (i.e., total coliform and E. coli bacteria). The U.S. EPA anticipates greater public health protection as the rule requires water systems that are vulnerable to microbial contamination to identify and fix problems. Water systems that exceed a specified frequency of total coliform occurrences are required to conduct an assessment to determine if any sanitary defects exist. If found, these must be corrected by the water system. The state Revised Total Coliform Rule became effective July 1, 2021.

**Additional General Information on Drinking Water**

Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants. The drinking water provided exceeds some secondary drinking water standards. Secondary MCLs are set on the basis of aesthetics and have no known health effects associated with consumption. The presence of contaminants does not necessarily indicate that the water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the U.S. EPA’s Safe Drinking Water Hotline (1-800-426-4791).

Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care providers. U.S. EPA/Centers for Disease Control (CDC) guidelines on appropriate means to lessen the risk of infection by *Cryptosporidium* and other microbial contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791).

***Use Less Water, Spend Less Money***

* Stop Leaks – Check appliances and outside systems such as sprinklers for leaks. Get to know your water meter – it provides important information about consumption and leaks. Common leaks waste 10% of the water used in many homes.
* Replace Old Toilets – Toilet flushing is the top water user in the home. If you have not replaced your toilet in 10 years or more, you will benefit from the new high efficiency models. Check the internal flapper for leaks by adding a little food coloring to the tank. If the colored water shows up in the toilet bowl, it is time to replace the rubber flapper.
* Buy an efficient Clothes Washer - Washers are the second-largest water user in the home. New “Energy Star” certified models use 50% less water and energy per load.
* Visit our website www.idyllwildwater.com

Some of the above suggestions may save hundreds of dollars per year in water and energy costs. If you need more information, call us at (951) 659-2143.

**Terms and Abbreviations Used in this Report and Tables**

**Level 1 Assessment:** A Level 1 Assessment is a study of the water system to identify potential problems and determine (if possible) why total coliform bacteria have been found in our water system.

**Level 2 Assessment:** A Level 2 Assessment is a very detailed study of the water system to identify potential problems and determine (if possible) why an E. coli MCL violation has occurred and/or why total coliform bacteria have been found in our water system on multiple occasions.

**Public Health Goal (PHG)**: The level of a contaminant in drinking water below which there is no known or expected risk to health. PHGs are set by the California Environmental Protection Agency.

**Maximum Contaminant Level (MCL)**: The highest level of a contaminant that is allowed in drinking water. Primary MCLs are set as close to the PHGs (or MCLGs) as is economically and technologically feasible. Secondary MCLs are set to protect the odor, taste, and appearance of drinking water.

**Maximum Contaminant Level Goal (MCLG)**: The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs are set by the U.S. Environmental Protection Agency.

**Maximum Residual Disinfectant Level (MRDL):** The highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.

**Maximum Residual Disinfectant Level Goal (MRDLG):** The level of a drinking water disinfectant below which there is no known or expected risk to health. MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants.

**Primary Drinking Water Standard (PDWS)**: MCLs and MRDLs and treatment techniques (TTs) for contaminants that affect health, along with their monitoring and reporting requirements.

**Secondary Drinking Water Standards (SDWS):** MCLs for contaminants that affect taste, odor, or appearance of the drinking water. Contaminants with SDWSs do not affect the health at the MCL levels.

**Regulatory Action Level (AL)**: The concentration of a contaminant which, if exceeded, triggers treatment or other requirements that a water system must follow.

**Secondary Maximum Contaminant Level (SMCL):** Non-enforceable guidelines regarding chemicals that may cause cosmetic or aesthetic effects in drinking water.

**Treatment Technique (TT):** A required process intended to reduce the level of a contaminant in drinking water.

**Variances and Exemptions:** Permissions from the State Water Resources Control Board (State Board) to exceed an MCL or not comply with a treatment technique under certain conditions.

**N/A:** Not applicable

**N.D.**: Not detectable at testing limit

**ppm**: Parts per million or milligrams per liter (mg/L)

**ppb**: Parts per billion or micrograms per liter (µg/L)

**ppt:** Parts per trillion or nanograms per liter (ng/L)

**ppq:** Parts per quadrillion or picogram per liter (pg/L)

**pCi/L**: Picocuries per liter (a measure of radiation)

**About Your Drinking Water Qualit****y**

The following tables list all the drinking water contaminants that we detected from testing for the 2021 calendar year or earlier. The presence of these contaminants in the water does not necessarily indicate that the water poses a health risk. The state allows us to monitor for certain contaminants less than once a year because the concentrations of these contaminants are not expected to vary significantly from year to year. Some of the data, though representative of the water quality, are more than one year old.

**Drinking Water Contaminants Detected**

Tables 1,1A, 2, 3, 4, 5, 6, 7 and 8 list all the drinking water contaminants that were detected during the most recent sampling for the constituent. The presence of these contaminants in the water does not necessarily indicate that the water poses a health risk. The State Board allows us to monitor for certain contaminants less than once per year because the concentrations of these contaminants do not change frequently. Some of the data, though representative of the water quality, are more than one year old. Any violation of an AL, MCL, MRDL, or TT is asterisked. Additional information regarding the violation is provided later in this report.

**Table 1. Sampling Results Showing the Detection of Coliform Bacteria**

| **Microbiological Contaminants** | **Highest No. of Detections** | **No. of Months in Violation** | **MCL** | **MCLG** | **Typical Source of Bacteria** |
| --- | --- | --- | --- | --- | --- |
| *E. coli* | 2021 | 0 | (a) | 0 | Human and animal fecal waste |

1. Routine and repeat samples are total coliform-positive and either is *E. coli*-positive, or system fails to take repeat samples following *E. coli*-positive routine sample or system fails to analyze total coliform-positive repeat sample for *E. coli*.

**Table 1.A. Compliance with Total Coliform MCL between January 1 - December 31, 2021 (inclusive)**

| **Microbiological Contaminants** | **Highest No. of Detections** | **No. of Months in Violation** | **MCL** | **MCLG** | **Typical Source of Bacteria** |
| --- | --- | --- | --- | --- | --- |
| Total Coliform Bacteria | 2 | 1 | 1 positive monthly sample | 0 | Naturally present in the environment |
| Fecal Coliform and *E. coli* | 2021 | 0 | 0 | None | Human and animal fecal waste |

1. For systems collecting fewer than 40 samples per month: two or more positively monthly samples is a violation of the total coliform MCL

For violation of the total coliform MCL, include potential adverse health effects, and actions taken by water system to address the violation: The sample was not sampled downstream or upstream, but it was sampled and came back negative. The procedures were not followed correctly. Now the proper procedures have been put into place and will be followed from now on.

**Table 2: Sampling Results Showing Detection of Lead and Copper (2021)**

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| **Lead and Copper (unit of measure)** | **Sample Date** | **No. of Samples Collected** | **90th**  **Percentile Level Detected** | **No. of Sites Exceeding AL** | **AL** | **PHG** | **Typical Source of Contaminant** |
| Lead (ppb) | 2019 | 10 | 5 | None | 15 | 0.2 | Internal corrosion of household water plumbing systems; erosion of natural deposits |
| Copper (ppm) | 2019 | 10 | 0.44 | None | 1.3 | 0.3 | Internal corrosion of household water plumbing systems; erosion of natural deposits; leaching from wood preservatives |

No schools requested lead sampling during 2021.

**Table 3: Sampling Results for Sodium and Hardness**

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Chemical or Constituent**  **(unit of measure)** | **Sample Date** | **Level Detected** | **Range of Detections** | **MCL** | **PHG**  **(MCLG)** | **Typical Source of Contaminant** |
| Sodium (ppm) | 2019 - 2021 | 18.25 | 12 - 22 | None | None | Salt present in the water and is generally naturally occurring |
| Hardness (ppm) | 2019 - 2021 | 34.4 | 26 - 36 | None | None | Sum of polyvalent cations present in the water, generally magnesium and calcium, and usually naturally occurring |

**Table 4: Detection of Contaminants with a Primary Drinking Water Standard**

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Chemical or Constituent**  **(unit of measure)** | **Sample Date** | **Level Detected** | **Range of Detections** | **MCL**  **[MRDL]** | **PHG**  **(MCLG)**  **[MRDLG]** | **Typical Source of Contaminant** |
| Chlorine (ppm) | 2021 | 1.5 | .02 – 4.0 | 4.0  (as Cl2) [MRDL] | 4  (as Cl2) [MRDLG] | Drinking water disinfectant added for treatment |
| Total Trihalomethanes (ppb) | 2021 | 74.3 | 25 – 90 | 80 | N/A | By-product of drinking water disinfection |
| Haloacetic Acids (ug/L) | 2021 | 28.3 | 9.9 – 37.3 | 60 | N/A | By-product of drinking water disinfection |
| Uranium (pCi/L) | 2019 - 2021 | 6.04 | 1.79 | 20 | .43 | Erosion of natural deposits |
| Nitrate as N (ppm) | 2021 | .37 | ND – 1.0 | 10 | 10 | Leaching from natural deposits |

**A picture containing indoor

Description automatically generated**

**A picture containing floor, indoor, room, furniture

Description automatically generated**

**Water Treatment Facility piping.**

**Aeration process for raw water prior to treatment.**

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Chemical or Constituent**  **(unit of measure)** | **Sample Date** | **Level Detected** | **Range of Detections** | **SMCL** | **PHG (MCLG)** | **Typical Source of Contaminant** |
| Total Dissolved Solids (ppm) | 2019 - 2021 | 115.4 | 83 – 180 | 1,000 | None | Runoff/leaching of natural deposits |
| Chloride (ppm) | 2019 - 2021 | 12.3 | 2.8 – 29 | 500 | None | Runoff/leaching of natural deposits |
| Sulfate (ppm) | 2019 - 2021 | 2.04 | .53 – 8 | 500 | None | Runoff/leaching of natural deposits |
| Specific Conductance (us/cm) | 2019 - 2021 | 170 | 59 – 250 | 1,600 | None | Substances that form ions when in water |
| Turbidity (NTU) | 2019 - 2021 | 30.6 | 0 – 78 | 5 | None | Soil runoff |
| Aluminum (ppb) | 2019 - 2021 | 103.1 | ND – 390 | 200 | 600 | Erosion of natural deposits |
| Iron (ppb) | 2019 - 2021 | **3,284.8** | **ND – 33,000** | 300 | None | Leaching from natural deposits |
| Color (color units) | 2019 - 2021 | 3.7 | ND – 30 | 15 | None | Naturally occurring organic materials |

**Table 5: Detection of Contaminants with a Secondary Drinking Water Standard**

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **Chemical or Constituent (reporting units)** | **Sample Date** | **Level Detected** | **Range of Detections** | **Notification Level** | **Health Effects** |
| Bicarbonate (mg/L) | 2019 - 2021 | 58.7 | 43 - 100 | N/A | N/A |
| Alkalinity  (mg/L) | 2019 - 2021 | 64.55 | 46 - 100 | N/A | N/A |
| Calcium  (mg/L) | 2019 - 2021 | 14.9 | 8.3 - 27 | N/A | N/A |
| pH (pH units) | 2019 - 2021 | 7.1 | 6.8 – 7.8 | N/A | N/A |
| Magnesium (mg/L) | 2019 - 2021 | 1.9 | ND – 4 | N/A | N/A |

**Table 6: Detection of Unregulated Contaminants**

## 

## Summary Information for Violation of a MCL, MRDL, AL, TT, or Monitoring and Reporting Requirement

“We are required to monitor your drinking water for specific contaminants on a regular basis. Results of regular monitoring are an indicator of whether your drinking water meets health standards. During December 2021, we did not complete all monitoring for coliform bacteria, and therefore, cannot be sure of the quality of your drinking water during that time”.

Table 7. Violation of a MCL, MRDL, AL, TT or Monitoring Reporting Requirement

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Violation** | **Explanation** | **Duration** | **Actions Taken to Correct Violation** | **Health Effects Language** |
| Citation | Samples were taken on a windy day, with rain. Did not resample properly. | 1 month | Completed actions required by the state. | Coliforms are bacteria that are naturally present in the environment and are used as an indicator that other, potentially harmful, bacteria may be present. Coliforms were found in more samples than allowed and this was a warning of potential problems. |

1. **For Water Systems Providing Groundwater as a Source of Drinking Water**

| **Microbiological Contaminants (complete if fecal indicator detected)** | **Total No. of Detections** | **Sample Dates** | **MCL [MRDL]** | **PHG (MCLG) [MRDLG]** | **Typical Source of Contaminant** |
| --- | --- | --- | --- | --- | --- |
| *E. coli* | 0 | 2021 | 0 | 0 | Human and animal fecal waste |
| Enterococci | 0 | 2021 | TT | N/A | Human and animal fecal waste |
| Coliphage | 0 | 2021 | TT | N/A | Human and animal fecal waste |

## Summary Information for Fecal Indicator-Positive Groundwater Source Samples, Uncorrected Significant Deficiencies, or Violation of a Groundwater TT

## Level 1 or Level 2 Assessment Requirement not Due to an *E. coli* MCL Violation

## Coliforms are bacteria that are naturally present in the environment and are used as an indicator that other, potentially harmful, waterborne pathogens may be present or that a potential pathway exists through which contamination may enter the drinking water distribution system. We found coliforms indicating the need to look for potential problems in water treatment or distribution. When this occurs, we are required to conduct assessment(s) to identify problems and to correct any problems that were found during these assessments.

The water system shall include the following statements, as appropriate:

During the past year we were required to conduct a Level 1 assessment. One Level 1 assessment(s) were completed. In addition, we were required to take four (4) corrective actions and we completed the four actions.

Logo

Description automatically generated with low confidence

A solar panel on a field

Description automatically generated with low confidence

**Solar Panel at Water Treatment Facility reduces District energy costs.**

**District crews are resolute employees and repair leaks throughout the year.**

A picture containing outdoor, ground, colorful

Description automatically generated A picture containing outdoor

Description automatically generated

**Before recoating**

A picture containing building

Description automatically generated

**South Ridge water storage tank repairs and recoating.**

A picture containing ceiling, indoor, Ferris wheel, ride

Description automatically generated

**After recoating**



**IDYLLWILD WATER DISTRICT**

**2021 Consumer Confidence Report**

**June 2022**

**IDYLLWILD WATER DISTRICT** PRSRT STD

**25945 HIGHWAY 243** AUTO

**P.O. BOX 397** U.S.POSTAGE

**IDYLLWILD, CA 92549-0397** PAID

San Jacinto, CA

Permit No. 51

**Board of Directors**

Dr. Charles Schelly, President

Peter Szabadi, Vice President

Steven Kunkle, Director

Les Gin, Director

Steve Olson, Director