


[bookmark: _Toc58336712]2025 Consumer Confidence Report
[bookmark: _Toc58336713]Water System Information
[bookmark: _Toc58336714]Water System Name: Mhc Tt Inc. (dba Pio Pico)
Report Date: 6/25/2026
Type of Water Source(s) in Use: Groundwater
Name and General Location of Source(s): Wells 01 and 02 are located in the Pio Pico South area near the resort Office; Well 06 is located in the Pio Pico North area at the north end of the resort (near the North Lodge). The resort is located off Otay Lakes Road in Jamul, San Diego County.
Drinking Water Source Assessment Information: Completed in 2002 and 2020. Available upon request from the San Diego Division of Drinking Water. Please call (619) 525-4159 for more information.
Time and Place of Regularly Scheduled Board Meetings for Public Participation: N/A
For More Information, Contact: Sheila Ortmeir at 619-421-9723
About This Report
We test the drinking water quality for many constituents as required by state and federal regulations.  This report shows the results of our monitoring for the period of January 1 to December 31, 2025, and may include earlier monitoring data.
Importance of This Report Statement in Five Non-English Languages (Spanish, Mandarin, Tagalog, Vietnamese, and Hmong)
[bookmark: _Toc58336715]Language in Spanish: Este informe contiene información muy importante sobre su agua para beber. Favor de comunicarse con Mhc Tt Inc. (dba Pio Pico) al 619-421-9723 para asistirlo en español.

Terms Used in This Report
	Term
	Definition

	Level 1 Assessment
	A Level 1 assessment is a study of the water system to identify potential problems and determine (if possible) why total coliform bacteria have been found in our water system.

	Level 2 Assessment
	A Level 2 assessment is a very detailed study of the water system to identify potential problems and determine (if possible) why an E. coli MCL violation has occurred and/or why total coliform bacteria have been found in our water system on multiple occasions.

	Maximum Contaminant Level (MCL)
	The highest level of a contaminant that is allowed in drinking water.  Primary MCLs are set as close to the PHGs (or MCLGs) as is economically and technologically feasible.  Secondary MCLs are set to protect the odor, taste, and appearance of drinking water.

	Maximum Contaminant Level Goal (MCLG)
	The level of a contaminant in drinking water below which there is no known or expected risk to health.  MCLGs are set by the U.S. Environmental Protection Agency (U.S. EPA).

	Maximum Residual Disinfectant Level (MRDL)
	The highest level of a disinfectant allowed in drinking water.  There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.

	Maximum Residual Disinfectant Level Goal (MRDLG)
	The level of a drinking water disinfectant below which there is no known or expected risk to health.  MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants.

	Primary Drinking Water Standards (PDWS)
	MCLs and MRDLs for contaminants that affect health along with their monitoring and reporting requirements, and water treatment requirements.

	Public Health Goal
(PHG)
	The level of a contaminant in drinking water below which there is no known or expected risk to health.  PHGs are set by the California Environmental Protection Agency.

	Regulatory Action Level
(AL)
	The concentration of a contaminant which, if exceeded, triggers treatment or other requirements that a water system must follow.

	Secondary Drinking Water Standards (SDWS)
	MCLs for contaminants that affect taste, odor, or appearance of the drinking water.  Contaminants with SDWSs do not affect the health at the MCL levels.

	Treatment Technique
(TT)
	A required process intended to reduce the level of a contaminant in drinking water.

	Variances and Exemptions
	Permissions from the State Water Resources Control Board (State Board) to exceed an MCL or not comply with a treatment technique under certain conditions.

	ND
	Not detectable at testing limit.

	ppm
	parts per million or milligrams per liter (mg/L)

	ppb
	parts per billion or micrograms per liter (µg/L)

	ppt
	parts per trillion or nanograms per liter (ng/L)

	ppq
	parts per quadrillion or picogram per liter (pg/L)

	pCi/L
	picocuries per liter (a measure of radiation)


[bookmark: _Toc58336716]Sources of Drinking Water and Contaminants that May Be Present in Source Water
The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells.  As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.
Contaminants that may be present in source water include:
Microbial contaminants, such as viruses and bacteria, that may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.
Inorganic contaminants, such as salts and metals, that can be naturally-occurring or result from urban stormwater runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.
Pesticides and herbicides, that may come from a variety of sources such as agriculture, urban stormwater runoff, and residential uses.
Organic chemical contaminants, including synthetic and volatile organic chemicals, that are byproducts of industrial processes and petroleum production, and can also come from gas stations, urban stormwater runoff, agricultural application, and septic systems.
Radioactive contaminants, that can be naturally-occurring or be the result of oil and gas production and mining activities.
Regulation of Drinking Water and Bottled Water Quality
In order to ensure that tap water is safe to drink, the U.S. EPA and the State Board prescribe regulations that limit the amount of certain contaminants in water provided by public water systems.  The U.S. Food and Drug Administration regulations and California law also establish limits for contaminants in bottled water that provide the same protection for public health.
[bookmark: _Toc58336717]About Your Drinking Water Quality
[bookmark: _Toc58336718][bookmark: _Hlk57994699]Drinking Water Contaminants Detected
Tables 1, 2, 3, 4, and 5 list all of the drinking water contaminants that were detected during the most recent sampling for the constituent.  The presence of these contaminants in the water does not necessarily indicate that the water poses a health risk.  The State Board allows us to monitor for certain contaminants less than once per year because the concentrations of these contaminants do not change frequently.  Some of the data, though representative of the water quality, are more than one year old.  Any violation of an AL, MCL, MRDL, or TT is asterisked.  Additional information regarding the violation is provided later in this report.
Table 1.  Sampling Results Showing the Detection of Lead and Copper
Complete if lead or copper is detected in the last sample set.

	Lead and Copper 
	Sample Date
	No. of Samples Collected
	90th Percentile Level Detected
	No. Sites Exceeding AL
	Range of Results
	AL
	PHG
	Typical Source of
Contaminant

	Lead (ppb)
	7/6/2023
	5
	ND
	0
	ND
	15
	0.2
	Corrosion of household plumbing systems; Erosion of natural deposits

	Copper (ppm)
	7/6/2023
	5
	0.059
	0
	ND – 0.068
	1.3
	0.3
	Internal corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives


Table 2.  Sampling Results for Sodium and Hardness
	Chemical or Constituent (and reporting units)
	Sample Date
	Level Detected (Average)
	Range of Detections
	MCL
	PHG (MCLG)
	Typical Source of Contaminant

	Sodium (ppm)
	6/1/2023
	130
	120 – 140
	None
	None
	Salt present in the water and is generally naturally occurring

	Hardness (ppm)
	6/1/2023
	307
	290 – 330
	None
	None
	Sum of polyvalent cations present in the water, generally magnesium and calcium, and are usually naturally occurring


Table 3.  Detection of Contaminants with a Primary Drinking Water Standard
	Chemical or Constituent
(and
reporting units)
	Sample Date
	Level Detected (Average)
	Range of Detections
	MCL [MRDL]
	PHG (MCLG) [MRDLG]
	Typical Source of Contaminant

	Nitrate as N (ppm)
	1/2/2025
	0.55
	ND – 0.55
	10
	10
	Runoff and leaching from fertilizer use; leaching from septic tanks and sewage; erosion of natural deposits

	Fluoride (mg/L)
	6/1/2023
	0.46
	0.18 – 0.46
	2.0
	1
	Erosion of natural deposits; water additive which promotes strong teeth; discharge from fertilizer and aluminum factories

	TTHM (ppb)
	1/2/2025
4/16/2025
7/2/2025
10/1/2025
	74.6
	34.7 – 121.5
	80
	N/A
	Byproduct of drinking water disinfection

	Total Haloacetic Acids (HAA5) (ppb)
	1/2/2025
4/16/2025
7/2/2025
10/1/2025
	14.6
	6.6 – 19.7
	60
	N/A
	Byproduct of drinking water disinfection

	Radium-226 (pCi/L)
	1/3/2024 (Well 6); 10/3/2023 (Wells 1 & 2)
	1.75 (Well 6); ND (Wells 1 & 2)
	ND – 1.75
	5
	0.05
	Erosion of natural deposits

	Radium-228 (pCi/L)
	1/3/2024 (Well 6); 10/3/2023 (Wells 1 & 2)
	1.29 (Well 6); ND (Wells 1 & 2)
	ND – 1.29
	5
	0.019
	Erosion of natural deposits


Table 4.  Detection of Contaminants with a Secondary Drinking Water Standard
	Chemical or Constituent (and reporting units)
	Sample Date
	Level Detected
	Range of Detections
	SMCL
	PHG (MCLG)
	Typical Source
of
Contaminant

	Specific Conductance (µS/cm)
	3/1/2023
	1133
	800 – 1300
	1600
	N/A
	Substances that form ions when in water; seawater influence

	Chloride (mg/L)
	3/1/2023
	226
	210 – 250
	500
	N/A
	Runoff/leaching from natural deposits; seawater influence

	Sulfate (mg/L)
	6/1/2023
	63.3
	59 – 72
	500
	N/A
	Runoff/leaching from natural deposits; industrial wastes

	Total Dissolved Solids (ppm)
	6/1/2023
	690
	630 – 720
	1000
	N/A
	Runoff/leaching from natural deposits

	Iron (µg/L)*
	Monthly 2025
	1000
	ND – 1000
	300
	N/A
	Leaching from natural deposits (treatment plant effluent)

	Manganese (µg/L)*
	Monthly 2025
	360
	ND – 360
	50
	N/A
	Leaching from natural deposits (treatment plant effluent)

	Odor (TON)
	6/1/2023
	1
	1
	3
	N/A
	Naturally occurring organic materials

	Turbidity (NTU)
	6/1/2023
	8.7 (Well 6)
	ND – 8.7
	5
	N/A
	Soil runoff


6Table 5.  Detection of Unregulated Contaminants
	Chemical or Constituent (and reporting units)
	Sample Date
	Level Detected
	Range of Detections
	Notification Level
	Health Effects 

	Boron (µg/L)
	6/1/2023
	126.6
	120 – 140
	1000
	Some people who drink water containing boron in excess of the notification level over many years could experience reproductive or developmental effects, based on studies in laboratory animals.


[bookmark: _Toc58336719]Additional General Information on Drinking Water
Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that the water poses a health risk.  More information about contaminants and potential health effects can be obtained by calling the U.S. EPA’s Safe Drinking Water Hotline (1-800-426-4791).
Some people may be more vulnerable to contaminants in drinking water than the general population.  Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections.  These people should seek advice about drinking water from their health care providers.  U.S. EPA/Centers for Disease Control (CDC) guidelines on appropriate means to lessen the risk of infection by Cryptosporidium and other microbial contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791).
Lead-Specific Language: Lead can cause serious health problems, especially for pregnant women and young children. Lead in drinking water is primarily from materials and components associated with service lines and home plumbing. Mhc Tt Inc. (dba Pio Pico) is responsible for providing high quality drinking water and removing lead pipes, but cannot control the variety of materials used in plumbing components in your home. You share the responsibility for protecting yourself and your family from the lead in your home plumbing. You can take responsibility by identifying and removing lead materials within your home plumbing and taking steps to reduce your family's risk. Before drinking tap water, flush your pipes for several minutes by running your tap, taking a shower, doing laundry or a load of dishes. You can also use a filter certified by an American National Standards Institute accredited certifier to reduce lead in drinking water. If you are concerned about lead in your water and wish to have your water tested, contact Mhc Tt Inc. (dba Pio Pico), Sheila Ortmeir at 619-421-9723. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available at http://www.epa.gov/safewater/lead.

* Iron and manganese are regulated by secondary maximum contaminant levels (SMCLs) of 300 µg/L and 50 µg/L — non-health-based standards that protect the taste, odor, and appearance of drinking water. The system's source wells are naturally high in iron and manganese and are treated through treatment plants before the water is delivered to customers. During 2025, iron and manganese in the treatment plant effluent exceeded their secondary MCLs in several months (see Table 7). The system is addressing this under Compliance Order 06_14_25C_004; January–March 2026 effluent results are non-detect for both.

Additional Special Language for Nitrate, Arsenic, Lead, Radon, and Cryptosporidium: N/A
State Revised Total Coliform Rule (RTCR): N/A
[bookmark: _Toc58336720]Summary Information for Violation of a MCL, MRDL, AL, TT, or Monitoring and Reporting Requirement
Table 6. Violation of a MCL, MRDL, AL, TT or Monitoring Reporting Requirement
	Violation
	Explanation
	Duration
	Actions Taken to Correct Violation
	Health Effects Language

	Iron and Manganese – Secondary MCL
	Iron and manganese in the treatment plant effluent exceeded their secondary (aesthetic) MCLs (300 µg/L for iron and 50 µg/L for manganese) during several months of 2025.
	Multiple months, January – August 2025
	The system is operating under Compliance Order 06_14_25C_004 (iron and manganese). Corrective actions include procurement and installation of a replacement automatic backwash valve at the treatment plant, commissioning, and enhanced backwash optimization, with continued monthly and quarterly monitoring and progress reporting. The system is scheduled to return to compliance by September 30, 2026; January–March 2026 effluent results are non-detect for iron and manganese.
	Iron and manganese are regulated by secondary standards set for aesthetic effects (discoloration, staining, and taste). The separate health-based level for manganese (500 µg/L) was not exceeded in the treated water. Infants and others who drink water containing high levels of manganese over a lifetime may experience effects on the nervous system.






