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2025 Consumer Confidence Report
DRINKING WATER


Water System Name:
Naval Air Station North Island (NASNI) 
&
 Naval Amphibious Base (NAB) 
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OUR COMMITMENT PROVIDING SAFE DRINKING WATER
Naval Base Coronado (NBC) is pleased to present our Water Quality Report, also referred to as the Consumer Confidence Report (CCR).  The CCR is an annual report containing data from water-quality testing performed during the past year and may include earlier monitoring data for some constituents.  
Last year, the water delivered to you met all U.S. Environmental Protection Agency (EPA) and State Water Board drinking water health standards.  Details within this report provide information on where we get our water, what is in your water, and how it compares to state standards that are considered safe for the public.  
 Este informe contiene información muy importante sobre su agua para beber.  Favor de comunicarse sobre Naval Air Station North Island (NASNI) & Naval Amphibious Base (NAB) Coronado System #3710750 a anne.l.bodel.civ@us.navy.mil para asistirlo en español.
Where do we get our water from?
NBC purchases water for NASNI and NAB from the City of San Diego, which is treated at the Alvarado Treatment Plant.  Water flows through a Navy-owned pipeline that supplies water to the distribution systems at NASNI and NAB.
The City of San Diego imports most of its raw surface water supply from the San Diego County Water Authority, which provides a blend of water from the Colorado River and the State Water Project.  Source water may include rivers, lakes, streams, ponds, reservoirs, springs, and wells.  As source water travels over the surface of the land or through the ground, it dissolves naturally occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.
Contaminants that may be present in source water include:
· Microbial contaminants, such as viruses and bacteria, which may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.
· Inorganic contaminants, such as salts and metals, that can be naturally occurring or result from urban stormwater runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.
· Pesticides and herbicides, which may come from a variety of sources such as agriculture, urban stormwater runoff, and residential uses.
· Organic chemical contaminants, including synthetic and volatile organic chemicals, which are byproducts of industrial processes and petroleum production, and can also come from gas stations, urban stormwater runoff, agricultural application, and septic systems.
· Radioactive contaminants, which can be naturally occurring or be the result of oil and gas production and mining activities.
Drinking water, including tap and bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily mean that water poses a health risk.  More information about contaminants and potential health effects can be obtained by contacting the Environmental Protection Agency by calling the Safe Drinking Water Hotline (800-426-4791) or visiting the website https://www.epa.gov/ground-water-and-drinking-water.

How do I know my water is safe?
To ensure that drinking water is safe, the EPA and the State Water Board prescribe regulations that limit the amount of certain contaminants in public water systems.  The U.S. Food and Drug Administration (FDA) regulations and California law also establish limits for contaminants in bottled water that provide the same protection for public health.
The City of San Diego conducts routine compliance sampling at the Alvarado Treatment Plant.  Every five (5) years, the City of San Diego conducts an assessment of their drinking water sources, also known as a Watershed Sanitary Survey.  A Watershed Sanitary Survey examines the potential sources of contaminants in the watersheds draining into reservoirs, and includes recommendations for managing these effects.  Information regarding the City of San Diego's Watershed Sanitary Survey can be accessed here:
             https://www.sandiego.gov/public-utilities/water-quality/watersheds/sanitary-survey 

NBC Public Works Department (PWD) contracts trained personnel to conduct compliance sampling within the NBC water distribution system for NASNI and NAB.  There are 48 routine sampling stations between NASNI and NAB, where water quality parameters are monitored that represent distribution areas.  Monitoring also occurs at water storage facilities located on both installations.
Some people may be more vulnerable to contaminants in drinking water than the general population.  Immuno-compromised people such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections.  These people should seek advice about drinking water from their health care providers.  EPA/Centers for Disease Control (CDC) guidelines on appropriate means to lessen the risk of infection by Cryptosporidium and other microbial contaminants are available from the EPA Safe Drinking Water Hotline (1-800-426-4791).
What about Lead?
If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children.  Potential sources of lead found in drinking water are primarily from materials and components associated with service lines and building plumbing.  Naval Base Coronado is responsible for providing high quality drinking water; however, some older plumbing components may contain a range of materials.

The Reduction of Lead in Drinking Water Act (RLDWA) went into effect on January 4, 2014.  The RLDWA has reduced the lead content allowed in water system and plumbing products by changing the definition of lead-free in Section 1417 of the Safe Drinking Water Act (SDWA) from not more than 8% lead content to not more than a weighted average of 0.25% lead with respect to plumbing materials and fixtures.  The SDWA prohibits the use of products that do not meet the lead-free requirement in the installation or repair of any public water system or facility providing water for human consumption.  
A Lead Service Line Inventory has been prepared for NASNI/NAB.  The inventory found no lead service lines in the distribution system and is available upon request by contacting the NBC Water Compliance Manager at (619) 545-1127 or victoria.y.nguyen.civ@us.navy.mil.

Lead can cause serious health effects in people of all ages, especially pregnant people, infants (both formula-fed and breastfed), and young children.  Because lead levels in drinking water may vary over time, lead exposure is possible even when your tap sampling results do not detect lead at one point in time.  You can help protect yourself by identifying and removing lead materials within your building's plumbing and taking steps to reduce your risk. 
Our Efforts to Minimize Your Exposure to Lead.
· Health and Safety Code (HSC) Section 116885. The Navy compiled an inventory of known materials for service lines in the distribution system.  No known lead service lines have been identified.
· Lead and Copper Rule Monitoring Program: In addition to the Priority Lead Sampling Program, the Navy is compliant with the lead and copper rule and conducts standard tap monitoring every 3 years at approved sample sites. 
How can I minimize exposure to lead?  
· Flush.  It is always a good idea to flush your faucet at work and/or at home, especially when water has been sitting for several hours (i.e., overnight or over a weekend).  You can minimize the potential for lead exposure by flushing your tap for 30 seconds to 2 minutes prior to utilizing it for consumption.  You may need to flush longer if your building has recently been shut down or experienced reduced occupancy.  Contact your Facility Manager or Assistant Public Works Officer for flushing guidance.
· Use cold water.  Hot water dissolves lead more quickly than cold water, so use cold water to prepare food and drinks.  
· Clean your aerator.  Debris can be trapped on the aerator screens on water outlets containing metals, especially if construction or plumbing work may have occurred in your area.  Simply twist off the aerator, tap and clean any debris which may be caught on the filtration screen, and reinstall.  
· Use a filter. Ensure filters are certified by an American National Standards Institute (ANSI) accredited certifier to reduce lead, which is effective in reducing lead exposures.  Follow the instructions provided with the filter to ensure the filter is used properly.  Make sure filters are replaced based on manufacturer specifications.

Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available at https://www.epa.gov/safewater/lead or contact 1-800-426-4791.

If you are concerned about lead in your water, contact your Facility Maintenance Specialist (FMS) or Liberty Housing (619) 556-8443.  For more information regarding Lead and Copper Monitoring, contact the NBC Water Compliance Program Manager at (619) 545-1127.
What about Lead at the Child Development Centers (CDC) and Youth Centers (YC)?  
In late 2024, EPA issued new requirements for community water systems to test drinking water for lead at elementary schools and childcare centers served by the system by 2027.  Since 2014, Navy policy, OPNAV 5090.1E, has required the Lead in Drinking Water Priority Areas (LIPA) testing program be conducted in the best interest of all staff and families served by the distribution system.  Any newly installed or repaired fixture identified during the audit must be sampled and tested for lead to ensure that lead-free products were installed.  Additionally, OPNAV 5090.1E was revised in 2024 to reflect a lower lead screening level of 10 parts per billion (ppb) to ensure the Navy is meeting the EPA’s revised lead action level.  For CY2025 LIPA Audit test results, please contact the NBC Water Compliance Program Manager at (619) 545-1127.  For more information regarding the Navy’s Lead in Priority Area Sampling Program, please visit https://cnrsw.cnic.navy.mil/Operations-and-Management/Environmental-Support/Drinking-Water-Quality-Information/Lead-in-Priority-Area-Sampling-Program/
Unregulated Contaminant Monitoring Rule (UCMR 5)
UCMR 5 sampling was conducted in 2025 as part of a nationwide study by EPA to assess the occurrence of unregulated contaminants.  These monitoring efforts help EPA determine whether additional drinking water standards are needed.  These contaminants are not currently subject to federal or state drinking water standards.  Of the 30 contaminants monitored, 29 were not detected above the UCMR 5 minimum reporting level (MRL); lithium was detected (see Table 4). 
For 2025 UCMR 5 monitoring results, please contact the NBC Drinking Water Program Manager at (619) 545-1130.
Summary Information for Violation of a MCL, MRDL, AL, NL, or TT
There were no primary MCL, MRDL, AL, NL, or TT violations for this system in 2025.  The CA secondary MCL exceedance for turbidity is noted in Table 3.
















	TERMS USED IN THIS REPORT

	Terms and Definitions
Action Level (AL): The concentration of a contaminant which, if exceeded, triggers treatment or other requirements that a water system must follow.
CA Secondary Maximum Contaminant Level (CA SMCL): MCL for secondary contaminants under CA regulations. Secondary MCLs are set to protect the odor, taste, and appearance of drinking water.
Detection Limit for Reporting (DLR): The lowest level of a contaminant that a lab can reliably measure and report, ensuring accurate and consistent reporting of contaminant levels in water samples.
Locational Running Annual Average (LRAA): is a four-quarter average at an individual sample location.  The LRAA for each location must be less than the MCL.  The highest LRAA of the year is reported.
Method Detection Limit (MDL): Lowest quantifiable concentration of a measured analyte detectable by the lab.
Maximum Contaminant Level (MCL): The highest level of a contaminant that is allowed in drinking water. MCLs are set as close to the MCLGs as feasible using the best available treatment technology. 
Maximum Contaminant Level Goal (MCLG): The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLs are set by the EPA.
Maximum Residual Disinfectant Level (MRDL): The highest level of a disinfectant allowed in drinking water.  There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.
Maximum Residual Disinfectant Level Goal (MRDLG): The level of a drinking water disinfectant below which there is no known or expected risk to health.  MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants.
	
Minimum Reporting Level (MRL): The lowest concentration of a contaminant that can be reliably measured and reported by the laboratory.
Primary Drinking Water Standards (PDWS): MCLs and MRDLs for contaminants that affect health along with their monitoring and reporting requirements, and water treatment requirements; these standards are enforceable.
Public Health Goal (PHG): The level of a contaminant in drinking water below which there is no known or expected risk to health.  PHGs are set by the California Environmental Protection Agency.
Running Annual Average (RAA): An average calculated over four consecutive quarters. The RAA for each quarter must be less than the MCL.  The highest RAA of the year is reported.
Secondary Drinking Water Standards (SDWS): MCLs for contaminants that affect taste, odor, or appearance of the drinking water.  Contaminants with SDWSs do not affect the health at the MCL levels and are not enforceable.
Treatment Technique (TT): A required process intended to reduce the level of a contaminant in drinking water.
Variances and Exemptions: Permissions from the State Water Resources Control Board (State Water Board) to exceed an MCL or not comply with a treatment technique under certain conditions.
Abbreviations and Units
ND: Not detected at testing limit
NTU: Nephelometric Turbidity Unit (a measure of turbidity)
ppb: parts per billion or micrograms per liter (µg/L)
ppm: parts per million or milligrams per liter (mg/L)



The water quality data for 2025 is summarized in the following tables.  Tables 1, 2, 3, and 4 list all the drinking water contaminants that were detected during the most recent sampling in treated drinking water.  The presence of these contaminants in the water does not necessarily indicate that the water poses a health risk.  The State Water Board allows certain contaminants to be monitored less than once per year because the concentration of these contaminants does not change frequently.  Some of the data, though representative of the water quality, are more than one year old.  
	TABLE 1 – SAMPLING RESULTS SHOWING THE DETECTION OF LEAD AND COPPER(b)

	
	Sample Date
	No. of Samples Collected
	90th Percentile Level Detected
	Range of Detections
	No. Sites Exceeding AL
	AL
	PHG
	CDC/YC Requesting Lead Sampling
	Typical Source of Contaminant

	Lead (ppb)
	27 Sep 2023
	20
	2.6
	ND–5.8

	0
	15
	0.2
	None to report
	Internal corrosion of household water plumbing systems; discharges from industrial manufacturers; erosion of natural deposits

	Copper (ppm)
	27 Sep 2023
	20
	0.73
	0.079–0.780

	0
	1.3
	0.3
	None to report
	Internal corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives

	(b) Per the Revised Lead and Copper Rule, triennial monitoring is allowed for systems whose monitoring indicates that lead levels are below ½ the AL.  
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TABLE 2 – DETECTION OF CONTAMINANTS WITH A PRIMARY DRINKING WATER STANDARD

	Chemical or Constituent
(and reporting units)
	Sample Year
(frequency)
	Level
Detected
(Average)
	Range of Detections
	MCL
[MRDL]
	PHG
(MCLG)
[MRDLG]
	Typical Source of Contaminant

	DISINFECTANT RESIDUAL AND DISINFECTANT BY-PRODUCTS AND PRECURSORS

	Chlorine Residual (as Cl2; ppm)
	2025
(monthly)
	RAA = 0.8541 RAA = 0.9912
	0.03–2.61
0.04–3.42
	[4.0]
	[4.0]
	Drinking water disinfectant added for treatment

	Total Trihalomethanes
(TTHM; ppb)
	2025
(quarterly)
	LRAA = 231
LRAA = 302
	14–291
25–382
	80
	(0)
	By-product of drinking water disinfectant

	Haloacetic Acids (HAA5; ppb)
	2025
(quarterly)
	LRAA = 7.61
LRAA = 11.52
	3.8–9.81
6.9–172
	60
	(0)
	By-product of drinking water disinfectant

	1NAS North Island results
2Naval Amphibious Base results

	CHEMICAL PARAMETERS

	Nitrite (as N; ppm)
	2025
	0.3831
0.1672
	ND–0.3831
ND–0.1672
	1
	1
	Runoff and leaching from fertilizer use; erosion of natural deposits

	1NAS North Island results
2Naval Amphibious Base results

	TABLE 3 – DETECTION OF CONTAMINANTS WITH A SECONDARY DRINKING WATER STANDARD

	Chemical or Constituent
(and reporting units)
	Sample Year
	Level
Detected
(Average)
	Range of Detections
	CA SMCL
	 MDL (DLR)
	Typical Source of Contaminant

	Color (CU)
	2025
	RAA = 0.961
RAA = 0.432
	ND–401
ND–72
	15
	1
	Naturally-occurring organic materials

	Odor-Threshold (OU)
	2025
	RAA = 0.271
 RAA = 0.1892
	ND–21
ND–22
	3
	(1)
	Naturally-occurring natural deposits

	Turbidity (NTU)(f)
	2025
	RAA = 0.511
RAA = 0.422
	0.1–111
0.1–1.32
	5
	0.10
	Soil runoff

	1NAS North Island results
2Naval Amphibious Base results
(f) At one NASNI sample site, one four-quarter running annual average (RAA) for turbidity exceeded the CA secondary MCL in 2025. NBC reported the exceedance to DDW and is continuing quarterly monitoring and follow-up.

	TABLE 4 – DETECTION OF UNREGULATED CONTAMINANTS (UCMR 5)(g) 

	Chemical or Constituent
(Reporting Units)
	Sample Year
	Level Detected
(Average)
	Range of Detections
	    UCMR5 MRL
	Typical Source of Contaminant

	Lithium (ppb)
	2025
	27.0
	25.2–28.8
	9
	Naturally-occurring element in drinking water originating from weathering of minerals at the subsurface.

	(g) Table 4 shows 2025 UCMR 5 results for contaminants detected at or above the minimum reporting level (MRL). These contaminants are not currently subject to federal or state drinking water standards.



Water Complaints
Does your water have an odd taste, color, odor, suspended solids, or do you suspect a water-related illness?  Does the filter on your fountain or faucet need to be changed?  Please contact your Facility Management Specialist, or Liberty Housing at (619) 556-8443, with details (i.e., building number, concern, complaint POC).

Where can I get more information on drinking water?
The City of San Diego produces an annual report detailing the sources of our water, where it is purchased from, and how it is treated, monitored and delivered.  This report is available online at
 
· https://www.sandiego.gov/public-utilities/water-quality/water-quality-reports

If you would like additional information on sampling and monitoring efforts at NASNI/NAB, please contact the Naval Base Coronado (NBC) Drinking Water Program Manager at 619-545-1130.

To access this report electronically, please visit the Commander, Navy Region Southwest website at:
https://cnrsw.cnic.navy.mil/Operations-and-Management/Environmental-Support/Drinking-Water-Quality-Information/
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