## 2019 Consumer Confidence Report

|  |  |  |  |
| --- | --- | --- | --- |
| Water System Name: | **California Men’s Colony** | Report Date: | June 2020 |

*We test the drinking water quality for many constituents as required by state and federal regulations. This report shows the results of our monitoring for the period of January 1 to December 31, 2019 and may include earlier monitoring data.*

**Este informe contiene información muy importante sobre su agua para beber. Favor de comunicarse [California Men’s Colony] a [*Hwy 1 North, San Luis Obispo California (805) 547-7926*] para asistirlo en español.**

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Type of water source(s) in use: | | Surface Water | | | | | |
| Name & general location of source(s): | | | California State Project Water; Whale Rock Reservoir, Cayucos, CA, and Chorro Reservoir | | | | |
|  | | | | | | | |
| Drinking Water Source Assessment information: | | | | *The source is considered to be most vulnerable to the following activities* | | | |
| *for which no associated contaminants have been detected: cattle grazing and historic mining operations in the watershed* | | | | | | | |
| Time and place of regularly scheduled board meetings for public participation: | | | | | Not applicable to this water system | | |
|  | | | | | | | |
| For more information, contact: | Michael Schwartz | | | | | Phone: | ( 805 ) 547-7557 |

|  |  |
| --- | --- |
| **TERMS USED IN THIS REPORT** | |
| **Maximum Contaminant Level (MCL)**: The highest level of a contaminant that is allowed in drinking water. Primary MCLs are set as close to the PHGs (or MCLGs) as is economically and technologically feasible. Secondary MCLs are set to protect the odor, taste, and appearance of drinking water.  **Maximum Contaminant Level Goal (MCLG)**: The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs are set by the U.S. Environmental Protection Agency (U.S. EPA).  **Public Health Goal (PHG)**: The level of a contaminant in drinking water below which there is no known or expected risk to health. PHGs are set by the California Environmental Protection Agency.  **Maximum Residual Disinfectant Level (MRDL)**: The highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.  **Maximum Residual Disinfectant Level Goal (MRDLG)**:The level of a drinking water disinfectant below which there is no known or expected risk to health. MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants.  **Primary Drinking Water Standards (PDWS)**: MCLs and MRDLs for contaminants that affect health along with their monitoring and reporting requirements, and water treatment requirements. | **Secondary Drinking Water Standards (SDWS)**:MCLs for contaminants that affect taste, odor, or appearance of the drinking water. Contaminants with SDWSs do not affect the health at the MCL levels.  **Treatment Technique (TT)**: A required process intended to reduce the level of a contaminant in drinking water.  **Regulatory Action Level (AL)**: The concentration of a contaminant which, if exceeded, triggers treatment or other requirements that a water system must follow.  **Variances and Exemptions**: Permissions from the State Water Resources Control Board (State Board) to exceed an MCL or not comply with a treatment technique under certain conditions.  **Level 1 Assessment**: A Level 1 assessment is a study of the water system to identify potential problems and determine (if possible) why total coliform bacteria have been found in our water system.  **Level 2 Assessment**: A Level 2 assessment is a very detailed study of the water system to identify potential problems and determine (if possible) why an *E. coli* MCL violation has occurred and/or why total coliform bacteria have been found in our water system on multiple occasions.  **ND**: not detectable at testing limit **ppm**: parts per million or milligrams per liter (mg/L) **ppb**: parts per billion or micrograms per liter (µg/L) **ppt**: parts per trillion or nanograms per liter (ng/L)  **ppq**: parts per quadrillion or picogram per liter (pg/L) **pCi/L**: picocuries per liter (a measure of radiation) |

**The sources of drinking water** (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells. As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.

**Contaminants that may be present in source water include:**

* *Microbial contaminants*, such as viruses and bacteria, that may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.
* *Inorganic contaminants*, such as salts and metals, that can be naturally-occurring or result from urban stormwater runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.
* *Pesticides and herbicides*, that may come from a variety of sources such as agriculture, urban stormwater runoff, and residential uses.
* *Organic chemical contaminants*, including synthetic and volatile organic chemicals, that are byproducts of industrial processes and petroleum production, and can also come from gas stations, urban stormwater runoff, agricultural application, and septic systems.
* *Radioactive contaminants*, that can be naturally-occurring or be the result of oil and gas production and mining activities.

**In order to ensure that tap water is safe to drink**, the U.S. EPA and the State Board prescribe regulations that limit the amount of certain contaminants in water provided by public water systems. The U.S. Food and Drug Administration regulations and California law also establish limits for contaminants in bottled water that provide the same protection for public health.

**Tables 1, 2, 3, 4, 5, and 6 list all of the drinking water contaminants that were detected during the most recent sampling for the constituent**. The presence of these contaminants in the water does not necessarily indicate that the water poses a health risk. The State Board allows us to monitor for certain contaminants less than once per year because the concentrations of these contaminants do not change frequently. Some of the data, though representative of the water quality, are more than one year old. Any violation of an AL, MCL, MRDL, or TT is asterisked. Additional information regarding the violation is provided later in this report.

|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Table 1 – SAMPLING RESULTS SHOWING the detection of coliform bacteria | | | | | | | | | | | | |
| **Microbiological Contaminants** (complete if bacteria detected) | | **Highest No. of Detections** | | **No. of Months in Violation** | | MCL | | | | | **MCLG** | **Typical Source of Bacteria** |
| Total Coliform Bacteria (state Total Coliform Rule) | | 1 | | 0 | | 1 positive monthly sample(a) | | | | | 0 | Naturally present in the environment |
| Fecal Coliform or *E. coli* (state Total Coliform Rule) | | 0 | | 0 | | A routine sample and a repeat sample are total coliform positive, and one of these is also fecal coliform or *E. coli* positive | | | | |  | Human and animal fecal waste |
| *E. coli*  (federal Revised Total Coliform Rule) | | 0 | | 0 | | (b) | | | | | 0 | Human and animal fecal waste |
| (a) Two or more positive monthly samples is a violation of the MCL  (b) Routine and repeat samples are total coliform-positive and either is *E. coli*-positive or system fails to take repeat samples following *E. coli*-positive routine sample or system fails to analyze total coliform-positive repeat sample for *E. coli*. | | | | | | | | | | | | |
| Table 2 – SAMPLING RESULTS SHOWING THE detection of Lead and copper | | | | | | | | | | | | |
| Lead and Copper (complete if lead or copper detected in the last sample set) | **Sample Date** | | **No. of Samples Collected** | | **90th Percentile Level Detected** | | **No. Sites Exceeding AL** | **AL** | **PHG** | **No. of Schools Requesting Lead Sampling** | | **Typical Source of Contaminant** |
| Lead (ppb) | 9/26/19 | | 30 | | ND | | 0 | 15 | 0.2 | 0 | | Internal corrosion of household water plumbing systems; discharges from industrial manufacturers; erosion of natural deposits |
| Copper (ppm) | 9/26/19 | | 30 | | ND | | 0 | 1.3 | 0.3 | Not applicable | | Internal corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives |

|  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TAble 3 – SAMPLING RESULTS FOR sodium and hardness | | | | | | | | | | | |
| **Chemical or Constituent** (and reporting units) | **Sample Date** | | | **Level Detected** | | **Range of Detections** | **MCL** | | **PHG (MCLG)** | **Typical Source of Contaminant** | |
| Sodium (ppm) | 2019 | | | 31.8 | | 7.4 - 50 | None | | None | Salt present in the water and is generally naturally occurring | |
| Hardness (ppm) | 2019 | | | 190 | | 82 - 210 | None | | None | Sum of polyvalent cations present in the water, generally magnesium and calcium, and are usually naturally occurring | |
| **TAble 4 – detection of contaminants with a Primary Drinking Water Standard** | | | | | | | | | | | |
| **Chemical or Constituent** (and reporting units) | **Sample Date** | | | **Level Detected** | | **Range of Detections** | **MCL [MRDL]** | | **PHG (MCLG) [MRDLG]** | **Typical Source of Contaminant** | |
| Aluminum (ppm) | 2019 | | | 0.33 | | ND – 0.87 | 1 | | 0.6 | Residue from water treatment process Erosion of natural deposits | |
| Arsenic (ppb) | 2019 | | | 1 | | ND – 3 | 10 | | .004 | Erosion of natural deposits; runoff from orchards; glass and electronics production wastes | |
| Barium (ppm) | 2019 | | | 0.01 | | ND - 0.027 | 1 | | 2 | Discharge of oil drilling wastes and from metal refineries; erosion of natural deposits | |
| Chromium Total (ppb) | 2019 | | | 3.7 | | ND - 11 | 50 | | 100 | Discharge from steel and pulp mills and chrome plating; erosion of natural deposits | |
| Flouride (ppm) | 2019 | | | 0.1 | | ND – 0.3 | 2.0 | | 1 | Erosion of natural deposits; water additive which promotes strong teeth; discharge from fertilizer and aluminum factories | |
| Gross Alpha Particle  (pCi/L) | 2019 | | | 5.3 | | 5.3 | 15 | | (0) | Erosion of natural deposits | |
| Turbidity NTU  (Treated) | 2019 | | | 0.05 | | 0.03 – 0.14 | TT | | N/A | Soil runoff | |
| Nickel (ppb) | 2019 | | | 19 | | ND – 57 | 100 | | 12 | Erosion of natural deposits; discharge from metal factories | |
| Selenium (ppb) | 2019 | | | 0.7 | | ND – 2.1 | 50 | | 30 | Discharge from petroleum, glass, and metal refineries; erosion of natural deposits; discharge from mines and chemical manufacturers; runoff from livestock lots (feed additive) | |
|  | | | | | | | | | | | |
| **DISTRIBUTION SYSTEM MONITORING** | | | | | | | | | | | |
| **Chemical or Constituent** (and reporting units) | **Sample Date** | | **Level Detected** | | **Range of Detections** | | | **MCL** | **PHG (MCLG)** | | Typical Source of Contaminant |
| Total Chlorine Residual  (Mg/l) | | 2019 | 1.78 | | 0.2 – 2.7 | | | 4.0 | 4.0 | | **Measurement of the disinfectant used in the production of drinking water** |
| Total Trihalomethanes  (ppb) | | 2019 | 35 | | |  | | --- | | 20 – 51 | | Highest LRAA: 37 | | | | 80 | n/a | | **By-product of drinking water chlorination** |
| Haloacetic Acids (ppb) | | 2019 | 15 | | |  | | --- | | 5 – 24 | | Highest LRAA: 17 | | | | 60 | n/a | | **By-product of drinking water chlorination** |
|  | | | | | | | | | | | |
|  |  | | |  | |  |  | |  |  | |
| **TAble 5 – detection of contaminants with a Secondary Drinking Water Standard** | | | | | | | | | | | |
| **Chemical or Constituent** (and reporting units) | **Sample Date** | | | **Level Detected** | | **Range of Detections** | **SMCL** | | **PHG (MCLG)** | Typical Source of Contaminant | |
| Aluminum (ppm) | 2019 | | | 0.33 | | ND – 0.87 | 1 | | 0.6 | Residue from water treatment process Erosion of natural deposits | |
| Corrosivity  (Aggressive Index) | 2019 | | | 12  Non-corrosive | | 12 | n/a | | n/a | Balance of hydrogen, carbon, and oxygen in water, affected by temperature and other factors. | |
| Chloride (ppm) | 2019 | | | 32 | | 11 - 142 | 500 | | n/a | Runoff/leaching from natural deposits; seawater influence | |
| Color (units)  (treated) | 2019 | | | 1 | | ND - 8 | 15 | | n/a | Naturally-occurring organic materials | |
| Copper (ppm) | 2018 | | | .001 | | ND - .0026 | 1.0 | | n/a | Internal corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives | |
| Iron, Total (ppb) | 2019 | | | 0.5 | | ND – 1.4 | 300 | | n/a | Leaching from natural deposits; industrial wastes | |
| Manganese (ppb) | 2019 | | | 16 | | ND - 39 | 50 | | n/a | Leaching from natural deposits | |
| pH (pH units)  (treated) | 2019 | | | 8.0 | | 7.7-8.7 | n/a | | n/a | Runoff/leaching from natural deposits; seawater influence | |
| Specific Conductance  (umhos/cm) | 2019 | | | 484 | | 131 - 709 | 1600 | | n/a | Substances that form ions when in water; seawater influence | |
| Sulfate (ppm) | 2019 | | | 49 | | 13 - 99 | 500 | | n/a | Runoff/leaching from natural deposits; industrial wastes | |
| Total Dissolved Solids  (ppm) | 2019 | | | 303 | | 250 - 400 | 1000 | | n/a | Runoff/leaching from natural deposits | |
| Zinc (ppm) | 2019 | | | .002 | | ND - .0057 | 5.0 | | n/a | Runoff/leaching from natural deposits; industrial wastes | |
|  |  | | |  | |  |  | |  |  | |
| **TAble 6 – detection of UNREGULATED CONTAMINANTS** | | | | | | | | | | | |
| **Chemical or Constituent** (and reporting units) | **Sample Date** | | | **Level Detected** | | **Range of Detections** | **Notification Level** | | | **Health Effects Language** | |
| Alkalinity (Total) as CaCO3 | 2019 | | | 163 | | 59 - 230 | n/a | | | Runoff/leaching from natural deposits; seawater influence | |
| Calcium (ppm) | 2019 | | | 25 | | 12 - 44 | n/a | | | Runoff/leaching from natural deposits; seawater influence | |
| Hardness (total)  As CaCO3 | 2019 | | | 190 | | 28- 278 | n/a | | | Leaching from natural deposits | |
| Magnesium (ppm) | 2019 | | | 32 | | 11 – 43 | n/a | | | Runoff/leaching from natural deposits; seawater influence | |
| Potassium (ppm) | 2019 | | | 2 | | ND – 3 | n/a | | | Runoff/leaching from natural deposits; seawater influence | |
| Total Organic Carbon  (toc) (treated) | 2019 | | | 2.2 | | 1.0 – 4.2 | n/a | | | Various natural and man-made sources | |
| Boron (ppb) | 2019 | | | 67 | | ND-200 | 1000 | | | Runoff/leaching from natural deposits. Agricultural and industrial waste. | |
| Vanadium (ppb) (c) | 2019 | | | 1.3 | | ND - 4 | 50 | | | Naturally occurring; has been found in association with hazardous waste sites. | |

**Additional General Information on Drinking Water**

Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants. The presence of contaminants does not necessarily indicate that the water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the U.S. EPA’s Safe Drinking Water Hotline (1-800-426-4791).

Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care providers. U.S. EPA/Centers for Disease Control (CDC) guidelines on appropriate means to lessen the risk of infection by *Cryptosporidium* and other microbial contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791).

Lead-Specific Language: If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children. Lead in drinking water is primarily from materials and components associated with service lines and home plumbing. [***ENTER WATER SYSTEM’S NAME HERE***] is responsible for providing high quality drinking water, but cannot control the variety of materials used in plumbing components. When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to 2 minutes before using water for drinking or cooking. [***OPTIONAL:*** If you do so, you may wish to collect the flushed water and reuse it for another beneficial purpose, such as watering plants.] If you are concerned about lead in your water, you may wish to have your water tested. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline (1-800-426-4791) or at <http://www.epa.gov/lead>.

|  |
| --- |
|  |
|  |

**Summary Information for Violation of a MCL, MRDL, AL, TT,  
or Monitoring and Reporting Requirement**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **VIOLATION OF A MCL, MRDL, AL, TT, OR MONITORING AND REPORTING REQUIREMENT** | | | | |
| **Violation** | **Explanation** | **Duration** | **Actions Taken to Correct the Violation** | **Health Effects Language** |
| **None** | **n/a** | **n/a** | **n/a** | **n/a** |
|  |  |  |  |  |

|  |
| --- |
|  |
|  |

**For Water Systems Providing Groundwater as a Source of Drinking Water**

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **TAble 7 – SAMPLING RESULTS SHOWING feCal indicator-positive groundwater source samples** | | | | | |
| **Microbiological Contaminants**  (complete if fecal-indicator detected) | **Total No. of Detections** | **Sample Dates** | **MCL [MRDL]** | **PHG (MCLG) [MRDLG]** | **Typical Source of Contaminant** |
| *E. coli* | n/a |  | 0 | (0) | Human and animal fecal waste |
| Enterococci | n/a |  | TT | N/A | Human and animal fecal waste |
| Coliphage | n/a |  | TT | N/A | Human and animal fecal waste |

**Summary Information for Fecal Indicator-Positive Groundwater Source Samples,  
Uncorrected Significant Deficiencies, or Groundwater TT**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **SPECIAL NOTICE OF FECAL INDICATOR-POSITIVE GROUNDWATER SOURCE SAMPLE** | | | | |
| No ground water was used as source water in 2019 | | | | |
|  | | | | |
|  | | | | |
|  | | | | |
| **SPECIAL NOTICE FOR UNCORRECTED SIGNIFICANT DEFICIENCIES** | | | | |
| No uncorrected deficiencies in 2019 | | | | |
|  | | | | |
|  | | | | |
|  | | | | |
| **VIOLATION OF GROUNDWATER TT** | | | | |
| **TT Violation** | **Explanation** | **Duration** | **Actions Taken to Correct the Violation** | **Health Effects Language** |
| None | n/a | n/a | n/a | n/a |
|  |  |  |  |  |

**For Systems Providing Surface Water as a Source of Drinking Water**

|  |  |
| --- | --- |
| **Table 8 - sampling results showing TREATMENT OF SURFACE WATER SOURCES** | |
| Treatment Technique (a)  (Type of approved filtration technology used) | Dual Media Sand Filtration |
| Turbidity Performance Standards (b)  (that must be met through the water treatment process) | Turbidity of the filtered water must:  1 – Be less than or equal to \_\_0.3\_\_\_ NTU in 95% of measurements in a month.  2 – Not exceed \_\_\_1.0\_\_ NTU for more than eight consecutive hours.  3 – Not exceed \_\_2.0\_\_ NTU at any time. |
| Lowest monthly percentage of samples that met Turbidity Performance Standard No. 1. | 100% |
| Highest single turbidity measurement during the year | 0.14 |
| Number of violations of any surface water treatment requirements | 0 |

(a) A required process intended to reduce the level of a contaminant in drinking water.

(b) Turbidity (measured in NTU) is a measurement of the cloudiness of water and is a good indicator of water quality and filtration performance. Turbidity results which meet performance standards are considered to be in compliance with filtration requirements.

**Summary Information for Violation of a Surface Water TT**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **VIOLATION OF A SURFACE WATER TT** | | | | |
| **TT Violation** | **Explanation** | **Duration** | **Actions Taken to Correct the Violation** | **Health Effects Language** |
| None | n/a | n/a | n/a | n/a |
|  |  |  |  |  |
|  |  |  |  |  |

**Summary Information for Operating Under a Variance or Exemption**

|  |
| --- |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |

**Summary Information for Federal Revised Total Coliform Rule**

**Level 1 and Level 2 Assessment Requirements**

**Level 1 or Level 2 Assessment Requirement not Due to an *E. coli* MCL Violation**

Coliforms are bacteria that are naturally present in the environment and are used as an indicator that other, potentially harmful, waterborne pathogens may be present or that a potential pathway exists through which contamination may enter the drinking water distribution system. We found coliforms indicating the need to look for potential problems in water treatment or distribution. When this occurs, we are required to conduct assessment(s) to identify problems and to correct any problems that were found during these assessments.

During the past year we were required to conduct [***1***] Level 1 assessment(s). [***1***] Level 1 assessment(s) were completed. In addition, we were required to take [***0***] corrective actions and we completed [***0*** of these actions.

During the past year [***0***] Level 2 assessments were required to be completed for our water system. [***0***] Level 2 assessments were completed. In addition, we were required to take [***0***] corrective actions and we completed [***0***] of these actions.

|  |
| --- |
|  |
|  |
|  |
|  |

**Level 2 Assessment Requirement Due to an *E. coli* MCL Violation**

*E. coli* are bacteria whose presence indicates that the water may be contaminated with human or animal wastes. Human pathogens in these wastes can cause short-term effects, such as diarrhea, cramps, nausea, headaches, or other symptoms. They may pose a greater health risk for infants, young children, the elderly, and people with severely-compromised immune systems. We found *E. coli* bacteria, indicating the need to look for potential problems in water treatment or distribution. When this occurs, we are required to conduct assessment(s) identify problems and to correct any problems that were found during these assessments.

During the past year [***0***] Level 2 assessments were required to be completed for our water system. In addition, we were required to take [***0***] corrective actions and we completed [***0***] of these actions.

|  |
| --- |
|  |
|  |
|  |
|  |

WATER SAVING TIPS FOR CONSUMERS

o Turn off the water when you brush your teeth - saves 3 gallons per day.

o Shorten your showers by two minutes - saves 5 gallons per shower.

o Wash only full loads of laundry - saves 15 to 50 gallons per load.

o Use the garbage can instead of the garbage disposal - saves 1 gallon per use.

Plumbing and Fixture Repairs or Upgrades

o Fix leaky faucets - Saves 20 gallons per day.

o Fix leaky toilets - Saves up to 78,000 gallons per year.

o Install high efficiency toilets - Saves up to 4 gallons per flush.

ACRONYMS:

AL Action Level

AWQR Annual Water Quality Report

CCR Consumer Confidence Report

CDC Centers for Disease Control

CDPH California Department of Public Health

CFR Code of Federal Regulations

CT Contact-Time

DBPP Disinfection Byproduct Precursor

DLR Detection Limit for Purposes of Reporting

DWSRF Drinking Water State Revolving Fund

EPA Environmental Protection Agency

FBRR Filter Backwash Recycling Rule

GWR Ground Water Rule

HAA5 Haloacetic Acids (five)

IESWTR Interim Enhanced Surface Water Treatment Rule

LCR Lead and Copper Rule

LPA Local Primacy Agency

LT1ESWTR Long-Term 1 Enhanced Surface Water Treatment Rule

LT2ESWTR Long-Term 2 Enhanced Surface Water Treatment Rule

LRAA Locational Running Annual Average

MCL Maximum Contaminant Level

MCLG Maximum Contaminant Level Goal

MDA Minimum Detectable Activity

mg/L milligrams per liter

mrem millirems

mrem/yr millirems per year

MRDL Maximum Residual Disinfectant Level

MRDLG Maximum Residual Disinfectant Level Goal

N/A or n/a Not Applicable

ND Non-Detected

NTU Nephelometric Turbidity Units

pCi/L picocuries per liter

PDWS Primary Drinking Water Standard

PHG Public Health Goal

ppb parts per billion

ppm parts per million

ppt parts per trillion

ppq parts per quadrillion

PWS Public Water System

RAA Running Annual Average

Stage 1 D/DBPR Stage 1 Disinfectants and Disinfection Byproducts Rule

Stage 2 D/DBPR Stage 2 Disinfectants and Disinfection Byproducts Rule

SWTR Surface Water Treatment Rule

TCR Total Coliform Rule

TOC Total Organic Carbon

TT Treatment Technique

TTHM Total Trihalomethanes

UCMR Unregulated Contaminant Monitoring Rule

USEPA United States Environmental Protection Agency