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[bookmark: _Toc58336713]Water System Information
Water System Name: Bridgehaven Park 
Report Date: May 13, 2026
Type of Water Source in Use: Surface Water
Name and General Location of Sources: Stream and Spring on Red Hill above Bridgehaven Park
For More Information, Contact: Erin O'Bryan at 916-441-6364 
[bookmark: _Toc58336714]About This Report
We test the drinking water quality for many constituents as required by state and federal regulations. This report shows the results of our monitoring for the period of January 1 to December 31, 2025, and may include earlier monitoring data.  
[bookmark: _Toc58336716]Sources of Drinking Water and Contaminants that May Be Present in Source Water
The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells.  As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.
Contaminants that may be present in source water include:
Microbial contaminants, such as viruses and bacteria, which may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.
Inorganic contaminants, such as salts and metals, which can naturally occur or result from urban stormwater runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.
Pesticides and herbicides, which may come from a variety of sources such as agriculture, urban stormwater runoff, and residential uses.
Organic chemical contaminants, including synthetic and volatile organic chemicals, which are byproducts of industrial processes and petroleum production, and can also come from gas stations, urban stormwater runoff, agricultural application, and septic systems.
Radioactive contaminants, which can naturally occur or be the result of oil and gas production and mining activities.
Regulation of Drinking Water and Bottled Water Quality
To ensure that tap water is safe to drink, the EPA and the State Water Board prescribe regulations which limit the amount of certain contaminants in water provided by public water systems.  FDA regulations and California law also establish limits for contaminants in bottled water which provide the same protection for public health.
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The following tables list the drinking water contaminants that were detected during the most recent sampling for the constituent.  The presence of these contaminants in the water does not necessarily indicate that the water poses a health risk.  The State Board allows us to monitor certain contaminants less than once per year because the concentrations of these contaminants do not change frequently.  Some of the data, though representative of the water quality, are more than one year old. Any violation is asterisked. Additional information regarding the violation is provided later in this report.
Table 1.  Sampling Results Showing the Detection of Coliform Bacteria
Coliform bacteria and e. coli were detected in the raw water but not in the finished (filtered and chlorinated) water provided to the customers. 
Table 2.  Sampling Results Showing the Detection of Lead and Copper

	Lead and Copper 
	Sample Date
	No. of Samples Collected
	90th Percentile Level Detected
	No. Sites Exceeding AL
	AL
	PHG
	Typical Source of
Contaminant

	Lead (ppb)
	7/8/24
	5
	0
	0
	15
	0.2
	Corrosion of household plumbing systems.  Erosion of natural deposits.

	Copper (ppm)
	7/8/24
	5
	144
	2
	1.3
	0.3
	Internal corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives


Table 3.  Sampling Results for Sodium and Hardness
	Chemical or Constituent (and reporting units)
	Sample Date
	Level Detected
	Range of Detections
	MCL
	PHG (MCLG)
	Typical Source of Contaminant

	Sodium (ppm)
	10/23/2025
	17.5
	16-19
	None
	None
	Salt present in the water and is generally naturally occurring

	Hardness (ppm)
	10/23/2025
	89.5
	79-100
	None
	None
	Sum of polyvalent cations present in the water, generally magnesium and calcium, and are usually naturally occurring


Table 4.  Contaminants with a Primary Drinking Water Standard. None exceeded the MCL.

	Chemical or Constituent (and reporting units)
	Sample Date
	Level Detected
	Range of Detections
	MCL
	Typical Source
of
Contaminant

	Chromium Hex
	10/23/25
	0.458
	0.056 – 0.86
	50
	Erosion of natural deposits

	Disinfection ByProducts

	TTHM
Total Trihalomethanes
	3/11/25
6/3/25
9/12/25
12/16/25
	1.6
4.1
86
53
	MCL 80



	Byproduct of drinking water disinfection

	HAA5
Sum of 5 Haloacetic Acids
	3/11/25
6/3/25
9/12/25
12/16/25
	ND
ND
48
61
	MCL 60
	Byproduct of drinking water disinfection


Table 5.  Detection of Contaminants with a Secondary Drinking Water Standard
Note: There are no PHGs, MCLGs, or mandatory standard health effects language for these constituents because secondary MCLs are set on the basis of aesthetic concerns. 

	Chemical or Constituent (and reporting units)
	Sample Date
	Level Detected
	Range of Detections
	MCL
	Typical Source
of
Contaminant

	Sulfate
	10/23/2025
	6.1
	3.2 - 9.0
	500
	Runoff/leaching from natural deposits;

	Iron
	10/23/25
	270
	<100 - 270
	300
	Leaching from natural deposits

	Chloride
	10/23/25
	22.5
	21 - 24
	500
	Runoff/leaching from natural deposits; seawater influence

	Manganese
	10/23/25
	42
	<2 - 42
	50
	Leaching from natural deposits


Table 6: Detection of Unregulated Contaminants.  None Detected
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Sampling Results Showing Treatment of Surface Water Sources
	Treatment Technique (a) 
	2  Harmsco 5 micron filters
1 Rosedale 3 micron bag filtration 
1 Rosedale 1.0 micron cartridge
Granular Activated Carbon Filter

	Turbidity Performance Standards (b) 
	Turbidity of the filtered water must:
1 – Be less than or equal to 0.2 NTU in 95% of measurements in a month.
2 – Not exceed 0.05 NTU for more than eight consecutive hours.
3 – Not exceed 1.0 NTU at any time.

	Lowest monthly percentage of samples that met Turbidity Performance Standard No. 1.
	8%

	Highest single turbidity measurement during the year
	3.62

	Number of violations of any surface water treatment requirements
	1*.  


(a)	A required process intended to reduce the level of contaminants in drinking water.
(b) Turbidity (measured in NTU) is a measure of the cloudiness of water.  We monitor it because it is a good indicator of water quality.  High turbidity can hinder the effectiveness of disinfectants.
*Due to our source being surface water, turbidity often exceeds the performance standard.  We are working with the state and an engineering company to secure a long-term solution.  Bridgehaven remains under a boil water notice until the turbidity exceedance is resolved. We have increased filtration and are diligent with daily maintenance to reduce turbidity.  We use spring water throughout the winter however turbidity increases during rain.  The spring flow is very limited and conservation is very important.  We are also working with the state for a long-term solution for an increased water supply.  Bridgehaven water quality is monitored daily, tested by the lab monthly, quarterly and annually and meets all standards and hasn’t violated a maximum contaminant level. 
 Additional General Information on Drinking Water
Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that the water poses a health risk.  More information about contaminants and potential health effects can be obtained by calling the EPA’s Safe Drinking Water Hotline (1-800-426-4791).
Some people may be more vulnerable to contaminants in drinking water than the general population.  Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections.  These people should seek advice about drinking water from their health care providers.  EPA/CDC guidelines on appropriate means to lessen the risk of infection by Cryptosporidium and other microbial contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791).


Lead in drinking water mainly comes from materials and components used in household plumbing and service lines. Bridgehaven Park provides high-quality drinking water and does not have lead pipes in its distribution system, however we cannot control the materials used in your home plumbing. To protect yourself and your family, identify and remove any lead-containing materials in your plumbing and take steps to reduce exposure. 
Elevated lead levels can cause serious health problems, especially for pregnant women and young children. Before using tap water for drinking, flush your pipes by showering, doing laundry, or washing dishes. You can also use a water filter certified by an American National Standards Institute-accredited certifier to reduce lead in drinking water.
For more information about lead in drinking water, testing methods, and ways to reduce exposure, call the Safe Drinking Water Hotline at (1-800-426-4791) or visit http://www.epa.gov/safewater/lead.


[bookmark: _Toc58336715]Terms Used in This Report
	Term
	Definition

	Maximum Contaminant Level (MCL)
	The highest level of a contaminant allowed in drinking water. Primary MCLs are set as close to the PHGs (or MCLGs) as is economically and technologically feasible. Secondary MCLs are set to protect the odor, taste, and appearance of drinking water.

	Maximum Contaminant Level Goal (MCLG)
	The level of a contaminant in drinking water below which there is no known or expected risk to health.  MCLGs are set by the U.S. Environmental Protection Agency (U.S. EPA).

	Primary Drinking Water Standards (PDWS)
	MCLs and MRDLs for contaminants that affect health along with their monitoring and reporting requirements, and water treatment requirements.

	Public Health Goal
(PHG)
	The level of a contaminant in drinking water below which there is no known or expected risk to health.  PHGs are set by the California Environmental Protection Agency.

	Regulatory Action Level
(AL)
	The concentration of a contaminant which, if exceeded, triggers treatment or other requirements that a water system must follow.

	Secondary Drinking Water Standards (SDWS)
	MCLs for contaminants that affect taste, odor, or appearance of the drinking water.  Contaminants with SDWSs do not affect the health at the MCL levels.

	Treatment Technique
(TT)
	A required process intended to reduce the level of a contaminant in drinking water.

	ND
	Not detectable at testing limit.

	ppm
	parts per million or milligrams per liter (mg/L)

	ppb
	parts per billion or micrograms per liter (µg/L)





SWS CCR	Revised January 2026

