## 2018 Consumer Confidence Report

| Water System Name: | J. D. Heiskell & Co System 5403048 | Report Date: | June 20, 2019 |
| --- | --- | --- | --- |

We test the drinking water quality for many constituents as required by state and federal regulations.  This report shows the results of our monitoring for the period of January 1 - December 31, 2018 and may include earlier monitoring data.

Este informe contiene información muy importante sobre su agua para beber. Favor de comunicarse J.D. Heiskell & Co.  a (559) 685-6592 para asistirlo en español.

这份报告含有关于您的饮用水的重要讯息。请用以下地址和电话联系 以获得中文的帮助: J.D. Heiskell & Co., 11518 Road 120, Pixley, CA (559) 685-6592. Ang pag-uulat na ito ay naglalaman ng mahalagang impormasyon tungkol sa inyong inuming tubig.  Mangyaring makipag-ugnayan sa J.D. Heiskell & Co.; 11518 Road 120, Pixley, CA o tumawag sa (559) 685-6592  para matulungan sa wikang Tagalog.

Báo cáo này chứa thông tin quan trọng về nước uống của bạn.  Xin vui lòng liên hệ J.D. Heiskell & Co. tại  (559) 685-6592 để được hỗ trợ giúp bằng tiếng Việt.

Tsab ntawv no muaj cov ntsiab lus tseem ceeb txog koj cov dej haus. Thov hu rau J.D. Heiskell & Co. ntawm                  (559) 685-6592  rau kev pab hauv lus Askiv.

| Type of water source(s) in use: | Groundwater NTNC |
| --- | --- |
| Name & location of source(s): | Source Name: Well 01 PS Code: 5403048-001, located; 11518 Road 120, Pixley |
| Drinking Water Source Assessment information: | http://swap.des.ucdavis.edu/TSinfo/output/ps5403048-001.pdf |
| Time and place of regularly scheduled board meetings for public participation: | Call for Appointment |
| For more information, contact: | Dawn L. Moninger | Phone: | (559) 685-6592 |
| TERMS USED IN THIS REPORT |
| Maximum Contaminant Level (MCL): The highest level of a contaminant that is allowed in drinking water. Primary MCLs are set as close to the PHGs (or MCLGs) as is economically and technologically feasible. Secondary MCLs are set to protect the odor, taste, and appearance of drinking water. Maximum Contaminant Level Goal (MCLG): The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs are set by the U.S. Environmental Protection Agency (U.S. EPA). Public Health Goal (PHG): The level of a contaminant in drinking water below which there is no known or expected risk to health. PHGs are set by the California Environmental Protection Agency. Maximum Residual Disinfectant Level (MRDL): The highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants. Maximum Residual Disinfectant Level Goal (MRDLG): The level of a drinking water disinfectant below which there is no known or expected risk to health. MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants. Primary Drinking Water Standards (PDWS): MCLs and MRDLs for contaminants that affect health along with their monitoring and reporting requirements, and water treatment requirements. | Secondary Drinking Water Standards (SDWS): MCLs for contaminants that affect taste, odor, or appearance of the drinking water. Contaminants with SDWSs do not affect the health at the MCL levels. Treatment Technique (TT): A required process intended to reduce the level of a contaminant in drinking water. Regulatory Action Level (AL): The concentration of a contaminant which, if exceeded, triggers treatment or other requirements that a water system must follow. Variances and Exemptions: State Board permission to exceed an MCL or not comply with a treatment technique under certain conditions. Level 1 Assessment: A Level 1 assessment is a study of the water system to identify potential problems and determine (if possible) why total coliform bacteria have been found in our water system. Level 2 Assessment: A Level 2 assessment is a very detailed study of the water system to identify potential problems and determine (if possible) why an E. coli MCL violation has occurred and/or why total coliform bacteria have been found in our water system on multiple occasions. ND: not detectable at testing limit ppm: parts per million or milligrams per liter (mg/L) ppb: parts per billion or micrograms per liter (µg/L) ppt: parts per trillion or nanograms per liter (ng/L) ppq: parts per quadrillion or picogram per liter (pg/L) pCi/L: picocuries per liter (a measure of radiation) |

The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells.  As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.

Contaminants that may be present in source water include:

- Microbial contaminants, such as viruses and bacteria, that may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.

- Inorganic contaminants, such as salts and metals, that can be naturally-occurring or result from urban stormwater runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.

- Pesticides and herbicides, that may come from a variety of sources such as agriculture, urban stormwater runoff, and residential uses.

- Organic chemical contaminants, including synthetic and volatile organic chemicals, that are by-products of industrial processes and petroleum production, and can also come from gas stations, urban stormwater runoff, agricultural application, and septic systems.

- Radioactive contaminants, that can be naturally-occurring or be the result of oil and gas production and mining activities.

In order to ensure that tap water is safe to drink, the USEPA and the state Department of Public Health (Department) prescribe regulations that limit the amount of certain contaminants in water provided by public water systems.  Department regulations also establish limits for contaminants in bottled water that provide the same protection for public health.

Tables 1, 2, 3, 4, and 5 list all of the drinking water contaminants that were detected during the most recent sampling for the constituent.  The presence of these contaminants in the water does not necessarily indicate that the water poses a health risk.  The Department allows us to monitor for certain contaminants less than once per year because the concentrations of these contaminants do not change frequently.  Some of the data, though representative of the water quality, are more than one year old.

| Table 1 – sampling results showing the detection of coliform bacteria |
| --- |
| Microbiological Contaminants (complete if bacteria detected) | Highest No. of Detections | No. of months in violation | MCL | MCLG | Typical Source of Bacteria |
| Total Coliform Bacteria (state Total Coliform Rule) | (In a mo.) 0 | 0 | More than 1 sample in a month with a detection | 0 | Naturally present in the environment |
| Fecal Coliform or E. coli (state Total Coliform Rule) | (In the year) 0 | 0 | A routine sample and a repeat sample detect total coliform and either sample also detects fecal coliform or E. coli | 0 | Human and animal fecal waste |
| E. coli (federal Revised Total Coliform Rule) | (In the year) 0 | 0 | (a) | 0 | Human and animal fecal waste |
| (a) Routine and repeat samples are total coliform-positive and either is E. coli-positive or system fails to take repeat samples following E. coli-positive routine sample or system fails to analyze total coliform-positive repeat sample for E. coli. |
| Table 2 – sampling results showing the detection of Lead and copper |
| Lead and Copper (complete if lead or copper detected in the last sample set) | No. of samples collected | 90th percentile level detected | No. sites exceeding AL | AL | PHG | Typical Source of Contaminant |
| Lead (ppb) 9/10/17 | 5 | 3.45 | 0 | 15 | 2 | Internal corrosion of household water plumbing systems; discharges from industrial manufacturers; erosion of natural deposits |
| Copper (ppm) 9/10/17 | 5 | .20 | 0 | 1.3 | 0.17 | Internal corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives |
| TAble 3 – sampling results for sodium and hardness |
| Chemical or Constituent (and reporting units) | Sample Date | Level Detected | Range of Detections | MCL | PHG (MCLG) | Typical Source of Contaminant |
| Sodium (ppm) | 7/6/11 | 54.3 | N/A | none | none | Salt present in the water and is generally naturally occurring |
| Hardness (ppm) | 7/6/11 | 86.6 | N/A | none | none | Sum of polyvalent cations present in the water, generally magnesium and calcium, and are usually naturally occurring |

*Any violation of an MC or AL is asterisked.  Additional information regarding the violation is provided later in this report.

| TAble 4 – detection of contaminants with a Primary Drinking Water Standard |
| --- |
| Chemical or Constituent (and reporting units) | Sample Date | Level Detected | Range of Detections | MCL [MRDL] | PHG (MCLG) [MRDLG] | Typical Source of Contaminant |
| Inorganic Contaminants |
| Barium (ppm) | 5/10/16 | 0.11 | N/A | 1 | 2 | Discharges of oil drilling wastes and from metal refineries; erosion of natural deposits |
| Nitrate (as nitrogen) (ppm) | 1/17/18 – 10/16/18 | 11.0* | 10.5 – 11.3 | 10 | 10 | Runoff and leaching from fertilizer use; leaching from septic tanks and sewage; erosion of natural deposits |
| Radioactive Contaminants |  |  |  |  |  |  |
| Gross Alpha Particle Activity (pCi/L) | 7/10/18 | 5.03 | N/A | 15 | (0) | Erosion of natural deposits |
| Uranium (pCi/L) | 7/10/18 | 5.70 | N/A | 20 | 0.43 | Erosion of natural deposits |
| Total Radium (pCi/L) | 2/14/17 – 11/8/17 | 1.1 | 0.34 – 1.75 | 5 | n/a | Erosion of natural deposits |
| Disinfection Byproducts, Disinfectant Residuals, and Disinfection Byproduct Precursors |
| Chlorine (Cl2) (ppm) | 1/17/18 – 12/5/18 | 1.6 | .17 – 2.96 | 4 (as Cl2) | 4 (as Cl2) | Drinking water disinfectant added for treatment |
| TTHMs (Total Trihalomethanes (ppb) | 8/20/18 | 12 | N/A | 80 | N/A | Byproduct of drinking water disinfection |
| HAA5 [Sum of 5 Haloacetic Acids] (µg/L) | 8/20/18 | 2.9 | N/A | 60 | N/A | Byproduct of drinking water disinfection |

| TAble 5 – detection of contaminants with a Secondary Drinking Water Standard |
| --- |
| Chemical or Constituent (and reporting units) | Sample Date | Level Detected | Range of Detections | MCL | PHG (MCLG) | Typical Source of Contaminant |
| Total Dissolved Solids (TDS) (ppm) | 7/6/11 | 300 | N/A | 1000 | None | Runoff/leaching from natural deposits |
| Specific Conductance (EC) µS/cm | 7/6/11 | 426 | N/A | 1600 | None | Substances that form ions when in water; seawater influence |
| Chloride (ppm) | 7/6/11 | 42.1 | N/A | 500 | None | Runoff/leaching from natural deposits; seawater influence |
| Sulfate (ppm) | 7/6/11 | 23 | N/A | 500 | None | Runoff/leaching from natural deposits; industrial wastes |
| Copper (ppm) | 7/6/11 | 0.02 | N/A | 1.0 | None | Internal corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives |
| Iron (ppb) | 7/6/11 | 24 | N/A | 300 | None | Leaching from natural deposits; industrial wastes |
| Zinc (ppm) | 7/6/11 | 0.11 | N/A | 5.0 | None | Runoff/leaching from natural deposits; industrial wastes |
| Odor-Threshold (Units) | 7/6/11 | 1 | N/A | 3 | None | Naturally-occurring organic materials |

There are no PHGs, MCLGs, or mandatory standard health effects language for these constituents because secondary MCLs are set on the basis of aesthetics.

| TAble 6 – detection of UNREGULATED CONTAMINANTS |
| --- |
| Chemical or Constituent (and reporting units) | Sample Date | Level Detected | Range of Detections | Notification Level | Health Effects Language |
| Hexavalent Chromium (ppb) | 12/16/14 | 2.0 | N/A | n/a | Discharge from electroplating factories, leather tanneries, wood preservation, chemical synthesis, refractory production, and textile manufacturing facilities; erosion of natural deposits |

Additional General Information on Drinking Water

Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that the water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the USEPA’s Safe Drinking Water Hotline (1-800-426-4791).

Some people may be more vulnerable to contaminants in drinking water than the general population.  Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care providers. USEPA/Centers for Disease Control (CDC) guidelines on appropriate means to lessen the risk of infection by Cryptosporidium and other microbial contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791).

The State allows us to monitor for some contaminants less than once per year because the concentrations of these contaminants do not change frequently.  Some of our data, though representative, are more than one year old

Barium:  Some people who drink water containing barium in excess of the MCL over many years may experience an increase in blood pressure.

Gross Alpha: Certain minerals are radioactive and may emit a form of radiation known as alpha radiation.  Some people who drink water containing alpha emitters in excess of the MCL over many years may have an increased risk of getting cancer.

Summary Information for Contaminants Exceeding an MCL, MRDL, or AL or
Violation of Any TT or Monitoring and Reporting Requirement

| VIOLATION OF A MCL, MRDL, AL, TT, OR MONITORING AND REPORTING REQUIREMENT |
| --- |
| Violation | Explanation | Duration | Actions Taken to Correct the Violation | Health Effects Language |
| The water system is in violation when Nitrate is found at levels that exceed the MCL of 10 mg/L. | Water samples were sampled quarterly in 2017 for nitrate. All samples exceeded the drinking water standard. The high levels of nitrate are due to Runoff and leaching from fertilizer use; leaching from septic tanks and sewage; erosion of natural deposits. | On going | POU (point of use) treatment devices have been installed for nitrate removal and are located at four sinks at the facility. The water system is on quarterly nitrate testing, and public notification of the quarterly nitrate result is posted on bulletin boards, posted near sinks and nitrate reminder emails are sent out. Bottled water and ice is provided for J.D. Heiskell & Co employees. | Nitrate in drinking water at levels above 10 mg/L is a health risk for infants of less than six months of age. Such nitrate levels in drinking water can interfere with the capacity of the infant’s blood to carry oxygen, resulting in serious illness; symptoms include shortness of breath and blueness of the skin. Nitrate levels above 10 mg/L may also affect the ability of the blood to carry oxygen in other individuals, such as pregnant women and those with specific enzyme deficiencies. If you are caring for an infant, or you are pregnant, you should ask advice from your health care provider. |