# 2025 Consumer Confidence Report

## Water System Information

Water System Name: Sonora Estates Mobile Home Community

Report Date: July 1, 2026

Type of Water Source(s) in Use: Groundwater

Name and General Location of Source(s): Wells No. 1 (-001) & No. 2 (-002). 22466 S. Airport Drive, Sonora, CA 95370.

Drinking Water Source Assessment Information: Completed in July 2001, the source is considered most vulnerable to the following activities not associated with any detected contaminants in the water supply: Mining operations, historic; airports - maintenance/fueling areas; wastewater treatment plant. A copy of the complete assessment is available or you may request a summary by contacting Merced District SWRCB - Division of drinking water (559) 447-3300.

Time and Place of Regularly Scheduled Board Meetings for Public Participation: [Enter Time and Place of Regularly Scheduled Board Meetings for Public Participation]

For More Information, Contact: Jessika Preston- 816-401-8213

## About This Report

We test the drinking water quality for many constituents as required by state and federal regulations. This report shows the results of our monitoring for the period of January 1 to December 31, 2025 and may include earlier monitoring data.

## Importance of This Report Statement in Five Non-English Languages (Spanish, Mandarin, Tagalog, Vietnamese, and Hmong)

Language in Spanish: Este informe contiene informaci6n muy importante sabre su agua para beber. Favor de comunicarse Sonora Estates Mobile Home Community a 22466 S. Airport Drive, Sonora, CA 95370 para asistirlo en espafiol.

Language in Mandarin: J!ffitliis-*1f�-F1t B"Jttffl 7.KB"J.m.JHrl)�,o if ffl �r	±-t!!±Jl::lD Egi,3ff,I(* [Enter Water System Name]��1icp;cs"Jmll;b: Sonora Estates Mobile Home Community 209-932-8747.

Language in Tagalog: Ang pag-uulat na ito ay naglalaman ng mahalagang impormasyon tungkol sa inyong inuming tubig. Mangyaring makipag-ugnayan sa Sonora Estates Mobile Home Community and Address] o tumawag sa 209-932-8747 para matulungan sa wikang Tagalog.

Language in Vietnamese: Bao cao nay ch(J,a thong tin quan tr9ng v� nLI'6'c u6ng cua bc;1n. Xin vui long lien h� Sonora Estates Mobile Home Community tc;1i 22466 S. Airport Drive, Sonora, CA 95370 d� dU'Q'C ho trQ' giup bang ti�ng Vi�t.

Language in Hmong: Tsab ntawv no muaj cov ntsiab lus tseem ceeb txog koj cov dej haus. Thov hu rau Sonora Estates Mobile Home Community ntawm 22466 S. Airport Drive, Sonora, CA 95370 rau kev pab hauv lus Askiv.

## Terms Used in This Report

| Term | Definition |
| --- | --- |
| Level 1 Assessment | A Level 1 assessment is a study of the water system to identify potential problems and determine (if possible) why total coliform bacteria have been found in our water system. |
| Level 2 Assessment | A Level 2 assessment is a very detailed study of the water system to identify potential problems and determine (if possible) why an E. coli MCL violation has occurred and/or why total coliform bacteria have been found in our water system on multiple occasions. |
| Maximum Contaminant Level (MCL) | The highest level of a contaminant that is allowed in drinking water. Primary MCLs are set as close to the PHGs (or MCLGs) as is economically and technologically feasible. Secondary MCLs are set to protect the odor, taste, and appearance of drinking water. |
| Maximum Contaminant Level Goal (MCLG) | The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs are set by the U.S. Environmental Protection Agency (U.S. EPA). |
| Maximum Residual Disinfectant Level (MRDL) | The highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants. |
| Maximum Residual Disinfectant Level Goal (MRDLG) | The level of a drinking water disinfectant below which there is no known or expected risk to health. MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants. |
| Primary Drinking Water Standards (PDWS) | MCLs and MRDLs for contaminants that affect health along with their monitoring and reporting requirements, and water treatment requirements. |
| Public Health Goal (PHG) | The level of a contaminant in drinking water below which there is no known or expected risk to health. PHGs are set by the California Environmental Protection Agency. |
| Regulatory Action Level (AL) | The concentration of a contaminant which, if exceeded, triggers treatment or other requirements that a water system must follow. |
| Secondary Drinking Water Standards (SOWS) | MCLs for contaminants that affect taste, odor, or appearance of the drinking water. Contaminants with SDWSs do not affect the health at the MCL levels. |
| Treatment Technique (TT) | A required process intended to reduce the level of a contaminant in drinking water. |
| Variances and Exemptions | Permissions from the State Water Resources Control Board (State Board) to exceed an MCL or not comply with a treatment technique under certain conditions. |
| ND | Not detectable at testing limit. |
| ppm | parts per million or milligrams per liter (mg/L) |
| ppb | parts per billion or micrograms per liter (µg/L) |

| Term | Definition |
| --- | --- |
| ppt | parts per trillion or nanograms per liter (ng/L) |
| ppq | parts per quadrillion or picogram per liter (pg/L) |
| pCi/L | picocuries per liter (a measure of radiation) |

Sources of Drinking Water and Contaminants that May Be Present in Source Water

The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells. As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.

Contaminants that may be present in source water include:

- Microbial contaminants, such as viruses and bacteria, that may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.

- Inorganic contaminants, such as salts and metals, that can be naturally-occurring or result from urban stormwater runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.

- Pesticides and herbicides, that may come from a variety of sources such as agriculture, urban stormwater runoff, and residential uses.

- Organic chemical contaminants, including synthetic and volatile organic chemicals, that are byproducts of industrial processes and petroleum production, and can also come from gas stations, urban stormwater runoff, agricultural application, and septic systems.

- Radioactive contaminants, that can be naturally-occurring or be the result of oil and gas production and mining activities.

## Regulation of Drinking Water and Bottled Water Quality

In order to ensure that tap water is safe to drink, the U.S. EPA and the State Board prescribe regulations that limit the amount of certain contaminants in water provided by public water systems. The U.S. Food and Drug Administration regulations and California law also establish limits for contaminants in bottled water that provide the same protection for public health.

## About Your Drinking Water Quality

Drinking Water Contaminants Detected

Tables 1, 2, 3, 4, 5, 6, 7, and 8 list all of the drinking water contaminants that were detected during the most recent sampling for the constituent. The presence of these contaminants in the water does not necessarily indicate that the water poses a health risk. The State Board allows us some constituent monitor for certain contaminants less than once per year because the concentrations of these contaminants do not change frequently.  Other contaminants such as Microbial Contaminates and PFAS contaminates have been detected in the water sources which require more frequent monitoring. Some of the data, though representative of the water quality, are more than one year old. Any violation of an AL, MCL, MRDL, or TT is asterisked. Additional information regarding the violation is provided later in this report.

### Table 1. Sampling Results Showing the Detection of Coliform Bacteria

Complete if bacteria are detected.

| Microbiological Contaminants | Highest No. of Detections | No. of Months in Violation | MCL | MCLG | Typical Source of Bacteria |
| --- | --- | --- | --- | --- | --- |
| E. coli | (In the year) 0 | 0 | (a) | 0 | Human and animal fecal waste |
| Total Coliform | (In the year) 0 | 5 | 5 | 5 | Naturally present in the Environment |

Health Effects: Coliforms are bacteria that are naturally present in the environment and are used as an indicator that other, potentially-harmful, bacteria may be present.  Coliforms were found in more samples than allowed and this was a warning of potential problems.

Corrective Actions:  After multiple Boil Order Notices had been sent out to Residence, a Level 1 Assessment was performed in August 2025 and submitted into the State Water Board.  Continued investigation and mitigation efforts were taken, which included Flushing with safe levels of Chlorination.  After several attempts to correct the source of Coliforms a Level 2 Assessment was performed by a State Water Board Representative and ultimately lead to the installation of Continuous Chlorination system at Well# 2 and Well# 1 is currently isolated unless of an emergency.

### Table 2. Sampling Results Showing the Detection of Lead and Copper

Complete if lead or copper is detected in the last sample set.

| Lead and Copper | Sample Date | No. of Samples Collected | 90th Percentile Level Detected | No. Sites Exceeding AL | AL | PHG | Typical Source of Contaminant |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Lead (ppb) | 7/28/2023 | 5 | 0 | 0 | 15 | 0.2 | Internal corrosion of household water plumbing systems; discharges from industrial manufacturers; erosion of natural deposits |
| Copper (ppm) | 7/28/2023 | 5 | 0.347 | 0 | 1.3 | 0.3 | Internal corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives |

### Table 3. Sampling Results for Sodium and Hardness

| Chemical or Constituent (and reporting units) | Sample Date | Level Detected | Range of Detections | MCL | PHG (MCLG) | Typical Source of Contaminant |
| --- | --- | --- | --- | --- | --- | --- |
| Sodium (ppm) | 12/13/22 | 3.575 | 3.53-3.62 | None | None | Salt present in the water and is generally naturally occurring |

| Hardness (ppm) | 12/13/22 | 312 | 310-314 | None | None | Sum of polyvalent cations present in the water, generally magnesium and calcium, and are usually naturally occurring |
| --- | --- | --- | --- | --- | --- | --- |

Table 4. Detection of Contaminants with a Primary Drinking Water Standard

| Chemical or Constituent (and reporting units) | Sample Date | Level Detected | Range of Detections | MCL [MRDL] | PHG (MCLG) [MRDLG] | Typical Source of Contaminant |
| --- | --- | --- | --- | --- | --- | --- |
| Chromium (ppb) | 12/13/22 | 5.75 | ND-11.5 | 50 | 10 | Erosion of natural deposits; discharge from steel & pulp mills and chrome plating |
| Nitrate (ppm) | 10/14/2025 Well #1 Well #2 | 2.2 2.3 | 2.46-2.70 | 10 | .4 | Runoff & leaching from fertilizer use; leaching from septic tanks & sewage; erosion of natural deposits |
| Fluoride (ppm) | 12/13/22 | 0.055 | ND - 0.11 | 2 | 0.1 | Erosion of natural deposits; water additive that promotes strong teeth; discharge from fertilizer and aluminum factories |
| Gross Alpha (pCi/L) | 5/4/21 | 0.3295 | 0.091-0.568 | 15 | 3 | Erosion of natural deposits |

### Table 5. Detection of PFAS or Per-Polyfluoroalkyl Substances

| PFAS | Sample Dates And Results (ng/L, ppt) | CCRDL “2,4” (ng/L, ppt) | Notification Level “3,4” (ng/L, ppt) | Response Level “3,4,5” (ng/L, ppt) | Public Health Goal “PHG” | Typical Source of Contaminant |
| --- | --- | --- | --- | --- | --- | --- |
| PFOA | 11/05/2026 Both Wells ND | 2.0 | 4.0 | 10 | 0.007 | See Detailed Explanation Below |
| PFOS | 11/05/2026 Both Wells ND | 2.0 | 4.0 | 40 | 1.0 | See Detailed Explanation Below |
| PFHxS | 11/05/2026 Both Wells ND | 2.0 | 3.0 | 10 |  | See Detailed Explanation Below |
| PFBS | 11/05/2026 Well# 1 = 3.1 Well# 2 = 3.4 | 2.0 | 500 | 5000 |  | See Detailed Explanation Below |
| PFHxA | 11/05/2026 Both Wells ND | 2.0 | 1,000 | 10,000 |  | See Detailed Explanation Below |

Notes:

ng/L = nanograms per liter ppt = parts per trillion

ND = not detected above the laboratory reporting limit

1 By US EPA Method 533.

2 The CCRDL is based on the US EPA UCMR 5 minimum reporting levels and listed in Exhibit B of the General Order (Order), dated March 4, 2024, and issued to the public water system. The Order can be accessed on the State WaterBoard’s Division of Drinking Water website at https://www.waterboards.ca.gov/drinking_water/certlic/drinkingwater/pfas_ddw_general_order/ .

3 A description of the notification and response level terminology can be found in the Order.

4 There are rules for rounding result values based on significant figures (the number of digits in a value that are known with a degree of accuracy) for the NLs and RLs. There are two significant figures for the CCRDLs, NLs and RLs starting from the first non-zero digit. Therefore, rounding will be applied to the sample result and then compared to the NL or RL to determine an exceedance. For example, PFOA result of 4.04 ng/L is rounded to 4.0 and is not greater than the NL of 4.0 ng/L. However, a PFOA result of 4.05 ng/L is rounded to 4.1 and does exceed the NL. Using the example above, both results of 4.0 and 4.1 ng/L would exceed the CCRDL of 2.0 ng/L.

5 An exceedance of the response level is based on a quarterly running annual average (QRAA), except for PFBS based on either a single sample or a confirmed sample. An explanation on how QRAA is calculated is provided in the 2024 Order.

6 Under the California Safe Drinking Water Act of 1996, public water systems with more than 10,000 service connections are required to prepare a report every three years for contaminants that exceed their respective public health goals (PHGs) (Health and Safety Code Section 116470[b]). For some PFAS, public water systems can only measure and report concentrations at levels above their PHG due to technological limitations, but some labs may still be able to quantify and report concentrations that are less than their CCRDL. Therefore, this should be considered a quantifiable level of risk.

Furthermore, the PWS source (WELL 1 & 2) with PS code of CA5500086_001_001 was analyzed for PFAS chemicals that cannot be specifically identified. The concentration of organofluorine (as adsorbable organic fluorine) is a proxy for total PFAS and was determined to be ND ng/L (nanograms per liter) via a method modeled after US EPA Method 1621.

The analytical lab report for the EPA Method 533 and modified 1621 analytical tests performed were on the sample collected date of 11/05/2025 from WELL 1 & 2.

ACTIONS REQUIRED

The PWS is required to report any PFAS detections above CCRDL in the annual Consumer Confidence Report (CCR) when PFAS is detected above CCRDL. Guidance is provided as follows depending on the PFAS that exceeds the CCRDL.

There will be a secondary follow up set of PFAS Tests ran in the month of June 2026.

Please note that there are thousands of different PFAS, some of which have been more widely used and studied than others. Scientific research suggests that exposure to certain PFAS may lead to adverse health outcomes. Research is still ongoing to determine how exposure to these different PFAS chemicals occurs and how they can affect human health.

Table 6. Detection of Contaminants with a Secondary Drinking Water Standard

| Chemical or Constituent (and reporting units) | Sample Date | Level Detected | Range of Detections | SMCL | PHG (MCLG) | Typical Source of Contaminant |
| --- | --- | --- | --- | --- | --- | --- |
| Bicarbonate Alkalinity (MG/L) | 12/13/22 | 336 | 331-341 |  |  | Carbonate containing rocks which can come from natural erosion or carbonate, runoff from natural deposits |
| Calcium (MG/L) | 12/13/22 | 76.05 | 75.6-76.5 |  |  | Naturally present |
| Chloride (MG/L) | 12/13/22 | 7.385 | 7.27-7.5 | 500 |  | Runoff/leaching from natural deposits; seawater influence |
| Magnesium (MG/L) | 12/13/22 | 29.6 | 29.4-29.8 |  | -- | Naturally present |
| Odor---Threshold (Ton) | 12/13/22 | 1 | 1 | 3 | 1 | Naturally-occurring organic materials |
| PH | 12/13/22 | 7.53 | 7.49-7.57 |  | -- |  |
| Specific Conductance (US) | 12/13/22 | 616.5 | 615-618 | 1600 |  | Substances that form ions when in water; seawater influence |
| Sulfate (MG/L) | 12/13/22 | 5.55 | 5.5-5.6 | 500 | .5 | Runoff/leaching from natural deposits; industrial wastes |
| Total Dissolved Solids [TDS] (MG/L) | 12/13/22 | 360 | 360 | 1000 |  | Runoff/leaching from natural deposits |
| Turbidity (NTU) | 12/13/22 | .0475 | .045-.05 | 5 | 0.1 | Soil runoff |

Table 7. Detection of Unregulated Contaminants

| Chemical or Constituent (and reporting units) | Sample Date | Level Detected | Range of Detections | Notification Level | Health Effects |
| --- | --- | --- | --- | --- | --- |
| None |  |  |  |  |  |

Additional General Information on Drinking Water

Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants. The presence of contaminants does not necessarily indicate that the water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the U.S. EPA's Safe Drinking Water Hotline (1-800-426-4791).

Some people may be more vulnerable to contaminants in drinking water than the general population. lmmuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care providers. U.S. EPA/Centers for Disease Control (CDC) guidelines on appropriate means to lessen the risk of infection by Cryptosporidium and other microbial contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791).

Lead-Specific Language: If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children. Lead in drinking water is primarily from materials and components associated with service lines and home plumbing. Sonora Estates Mobile Home Parks is responsible for providing high quality drinking water but cannot control the variety of materials used in plumbing components. When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to 2 minutes before using water for drinking or cooking. [Optional: If you do so, you may wish to collect the flushed water and reuse it for another beneficial purpose, such as watering plants.] If you are concerned about lead in your water, you may wish to have your water tested. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline (1-800-426-4791) or at http://www.epa.gov/lead.

Additional Special Language for Nitrate, Arsenic, Lead, Radon, and Cryptosporidium: Not Applicable. State Revised Total Coliform Rule (RTCR): Not Applicable.

Summary Information for Violation of a MCL, MRDL, AL, TT, or Monitoring and Reporting Requirement

Table 8. Violation of a MCL, MRDL, AL, TT or Monitoring Reporting Requirement

| Violation | Explanation | Duration | Actions Taken to Correct Violation |  |
| --- | --- | --- | --- | --- |
| 5 |  | 5 Separate Months | Listed within each contaminant table |  |

Actions Taken Water Systems Providing Groundwater as a Source of Drinking Water:

A Level 1 Assessment was submitted by John Ogle to the State Water Board in August 2025 due to multiple Positive Total Coliform test results on both Well#1 and #2.  Over the subsequent months Both Wells were disinfected, resealed, flushed multiple times, as well as the distributions system was flushed under chlorination and retested.  Total Coliform was absent for a period and came back off and on withing 2 months.  More sampling and mitigation occurred and ultimately became subject to a Level 2 Assessment by the State Water Board on Jan 28th 2026 with the mandate for continuous chlorination at Well #2 and turning off Well #1 until further notice.